## Sheet1
U.S. Hotel/Motel Carbon Monoxide Incidents - 1967 to date (10-1-2019)
| State | City | Date of incident | Victims | Name of facility | Chain/ member hotel | # of deaths | # of injured | # of child victims (18 and under) | Source of CO | Location of source | Incident details/notes
1 | OH | Boston Heights | 1967-11-18 | Betty Ann Bishop, 50 & sister Mary "Budd" Bishop, 56 (both deceased); Bruce, 22 (deceased) & wife Joan Plagman, 21 (injured) | Best Western Yankee Clipper Inn | Y | 3 | 100 |  | pool heater | basement laundry room | 11/18/1967 was a Saturday and over 500 people were at hotel for three differnent weekend events; a couple began to feel dizzy about 6:30pm and went to their room thinking they were catching the flu or ate something bad, at 11:30pm the man called the front desk for help because his wife had "fainted"; hotel sent a doctor who was onsite at a medical conference to their room - he was suspicious it was something they might have inhaled and called for an ambulance; at the same time the couple arrived to the emergency room, another couple arrived with the same symptoms from the hotel; CO was immediately suspected by an ER doctor and "every ambulance possible" was sent to hotel, along with "two hundred police officers, deputies and firefighters"; "hotel was seven stories, 21 rooms to a floor, and most were occupied"; room by room evacuation, guests were found "sprawled on floors, stretched across beds, moaning incoherently"; evacuation took two hours to complete; 3 people were discovered deceased, more than 100 people were injured, 60 hospitalized including six police officers who assisted with evacuation; carbon monoxide was traced to a swimming pool heater in a basement laundry room. "It's vent had been installed too closely to a fresh-air intake, which spread fumes through ducts to the upstairs"
2 | IL | Glen Ellyn | 1967-12-10 | Susan, 21 (deceased), & husband Anthony Grieshaber, 19 (injured), Mrs. Peter Decker, 45 (injured) & daughter Christine Decker, 17 (injured) | Holiday Inn | Y | 1 | 3 | 1 injured | heating unit |  | couple was staying on fourth floor and were found by clerk - she was deceased, he was unconscious and not expected to survive (unable to find information to confirm); woman and her daughter were staying in room on second floor were ill and taken to hospital - they had checked in around 11pm, woman was dizzy and nauseated when awakened by her daughter who was vomitting around 5am; motel was four-stories with 121 rooms and had been open for approximately one week; CO entered 14 rooms of hotel via "one or more loose-fitting joints in the metal tube chimney"
3 | OK | Lawton | 1967-12-28 | Linda F. Klinekole, 20 (deceased) | Hacienda Motel |  | 1 |  |  | heater | room | Victim found deceased in room
4 | OH | Ironton | 1968-01-03 | Walter Kelley, 43 (deceased) & wife Lucille Kelley, 41 (injured) |  |  | 1 | 1 |  | heater | office | victims were owners of the motel, husband found deceased in office and wife unconscious in adjoining bedroom
5 | CO | Aspen | 1968-12-22 | Jacquelyn Lazan, 24 (deceased), Joy Levy, 24 (injured) |  |  | 1 | 1 |  | heater | room | victims discovered by manager when they failed to check out; snow delayed injured victim's transport by helicopter to a treatment facility in Denver
6 | OK | Kellyville | 1968-12-31 | Richard Kuffel, 39 & wife, Darlene, 31, & their 5 children (all injured) |  |  |  | 7 | 5 injured | heater |  | victims were a couple and their 5 children; father was awakened by one of the children who was vomiting and crying - staggered to door and called for help; motel manager called ambulance; motel was newly opened
7 | CA | Norden | 1968-12-31 | Germaine Cliff, 18 (deceased) |  |  | 1 |  | 1 deceased | heater | room
8 | FL | Holly Hill | 1969-01-20 | William T. Byram, 54 & wife Martha, 35 (both deceased) | White Palms Motel |  | 2 |  |  | gas range | room | victims were permanent residents of the motel, discovered deceased in their room by a friend; cause determined to be a coffee pot that "boiled over, extinguishing the flame and allowing the gas to escape"
9 | AZ | Tucson | 1969-01-22 | James R. Johnston, 78 & wife Ethel, 77 (both deceased) | Gammill Motel |  | 2 |  |  | wall heater | room | victims discovered deceased in their room by a friend six days after they were last seen alive
10 | UT | Soldier Summit | 1969-02-11 | Jimmy Inskeep, 15 (deceased) |  |  | 1 |  | 1 deceased
11 | MN | Rochester | 1969-02-16 | Barbara Briggs, 21 (deceased) | Rochester Motel |  | 1 |  |  | gas heater | room | victim discovered by employer when she failed to show up at work two days in a row; she had been living at the motel
12 | TX | Victoria | 1969-02-22 | Sonia Medrano, 42 (deceased) & Ruben Cantu, 35 (injured) | Ranch Motel |  | 1 | 1 |  | heater | room | victims found by hotel manager at 3:00pm when they failed to check out at noon; woman found lying across bed, death approximated to be five hours earlier, and man was found unconscious on floor
13 | TX | El Paso | 1969-03-16 | Jerri, 32 (deceased) & husband Carl Cappel, 40 (injured) | Del Camino Motor Inn |  | 1 | 1 |  | furnace | room | victims discovered in their room when they failed meet traveling companions for breakfast, wife dead and husband unconscious; "a gas floor furnace in the room was found to have faulty pipes"; owner/manager subsequently charged with negligent homicide
14 | LA | Opelousas | 1969-12-24 | Mr. & Mrs. Everette Witt (both injured) |  |  |  | 2 |  |  |  | Fire Dept called to motel at 4:30am for "couple overcome with gas fumes"
15 | AR | Hot Springs | 1970-01-12 | Ernest J. Sander, 72 (deceased) & wife Emma Sander (injured) | Central Motel |  | 1 | 1 |  |  |  | victims checked into motel on 1/8, both ill and weak on 1/10 and doctor was called to hotel - initially diagnosed with possible pneumonia; on 1/12 owners and maid found husband unconscious and wife semi-conscious, transported to hospital where husband died 4 days later; source of CO undetermined - 2 gas heaters and a gas stove in room
16 | CA | Palm Springs | 1970-04-17 | Cyril Joseph Carey, 47 (deceased) | Sunshine Court Motel |  | 1 |  |  | heater
17 | FL | Delray Beach | 1970-11-26 | Lovella Hagabook, 45 (deceased) & husband (injured - no name or age listed) | Fred's Motel |  | 1 | 1 |  | charcoal heater | room
18 | CA | Hollywood | 1970-12-20 | Joseph Felice, 21 (injured), Phillip Martone, 21 (injured) | Chesterfield Hotel |  |  | 2 |  | heater | room | hotel employee found both victims unconscious in their room when they failed to check out; Felice was unconscious for six weeks and Martone was unconscious for five days until receiving appropriate treatment in for CO poisoing; both originally diagnosed as suffering from a drug overdose until they were transferred to a different medical facility where they were diagnosed with CO poisoning
19 | NM | Ruidoso | 1970-12-30 | John Grisham, 18 (deceased), Rod Krebbs, 17 (injured), Leland Parks, 17 (injured), Andrew Grub, 17 (injured), Keith Ellis, 18 (injured), Tim Ridpath, 18 (injured) | West Winds Motel |  | 1 | 5 | 1 deceased 5 injured | heating stove | room | victim was among 5 other teenagers who were staying at motel for skiing holiday; they all began experiencing nausea and headaches during first night's stay (Monday), completely slept thru next day (Tuesday), Wednesday 3 of them went out to get fresh air and something to eat and when they returned were unable to rouse victim, unable to locate manager so drove hospital to notify ambulance and police
20 | TX | Brownsville | 1970-12-31 | Felix Valadez, 23 (deceased) & fiancee Olga Perez, 20 (deceased) | Jayhawk Motel |  | 2 |  |  | heater | room | victims discovered deceased in room by motel owner - they had checked in at 12:30am and at 6pm owner went to room to inquire if they would be spending a second night
21 | OK | Hammon | 1971-01-14 | Woodrow "Buck" Snow, 55 (deceased) & wife Alene Snow, 50 (deceased) |  |  | 2 |  |  | wall heater | room | checked into hotel two days before being found deceased in room, along with their dog, by motel owners; woman's body found in bed, man on floor
22 | IN | East Chicago | 1971-01-20 | Ida Mae Watt, 11 (deceased) & mother Gloria Jean Cottrell, 33 (injured); George Stinnet (deceased), Gene Allen, 50 (deceased), Eli Wilkins, 30 (deceased) | Stevens Hotel |  | 4 | 9 | 1 deceased | furnace | basement | police called to hotel by hotel maintenance worker at 3:15am, surviving guests discovered "in various stages of unconsciousness"; police smashed windows to let in fresh air; two-foot section of "rotted" furnace flue pipe seperated from chimney was discovered on basement floor; per subsequent investigation and coroner's inquest, after hotel manager was taken to hospital for what was initally thought to be a heart attack around 9:30pm, then a second employee became ill with same symptoms a few hours later, the owner checked on the furnace - he then called furnace repairman at 2am to report flue pipe had fallen off and was instructed to shut off furnace and open basement windows; police testified furnace was running when they arrived and one basement window was open; hotel had been listed for sale two weeks prior; boiler had never been inspected according to Indianapolis city records
23 | CA | Pacifica | 1971-01-22 | Constance Joy Salciccia, 39 (deceased), Lawrence Owen Withey, 38 (deceased) | Rockaway Beach Motel |  | 2 |  |  | heater | room | victims discovered deceased in room by maid; woman's body found on bed, man on floor; 84 y/o man (hotel owner's father) had been discovered deceased in the room 9 days prior - had recently suffered a heart attack and autopsy determined he died of a collapsed lung, however cause of death was to be reviewed in light of deaths of the two subsequent victims
24 | IN | Portage | 1971-01-27 | Charles F. Sproul, 35 (deceased), and Patty Lee Young, 31 (deceased) | Gary Motel |  | 2 |  |  |  |  | victims discovered deceased in room by police when motel manager could not rouse them, cause attributed to a "faulty gas pipe"
25 | CO | Colorado Springs | 1971-03-21 | Mark A. Taylor, 17 (injured), Michael R. Todd, 17 (injured) | El Rancho Motel |  |  | 2 | 2 injured |  |  | victims were discovered unconscious in their room by a friend
26 | NY | Watertown | 1971-04-18 | Viki Jane Reed, 7 (deceased) & sister Tina Reed, 5 (injured); Mrs. Robert Barker (injured - first name and age not listed) & children Terry L. Barker, 13 (deceased), Tammy Barker, 8 (injured) | Hillside Motel |  | 2 | 3 | 2 deceased 2 injured |  |  | police were called after a neighbor boy found adult victim lying on the floor; adult victim and her husband listed as owners of motel and were caring for a friend's children who were the additional victims in the room; investigators determined "fumes escaped from a vent pipe that had broken apart"
27 | FL | Pensacola | 1971-11-24 | Ruth Struzulla, 53 (deceased), Ervin Barker, 53 (deceased) | Floridian Motel |  | 2 |  |  | heater | room | victims discovered deceased in room by motel employee
28 | SD | Ipswich | 1972-01-25 | Judith Huber, 23 (deceased) & Bernie Jahnig, 25 (deceased) | Ipswich Motel |  | 2 |  |  | heater |  | victims discovered deceased in room by motel owner; CO "may have been caused by ice clogging the motel chimney, preventing venting of carbon monoxide fumes from heating units"
29 | WY | Jackson | 1972-03-29 | William Palmer, 18 (deceased), Richard Kroiss, 18 (deceased), Dennis O'Connell, 16 (injured) | Sagebrush Motel |  | 2 | 1 | 2 deceased 1 injured | heater | room | victims discovered by motel owner after checking on them when they hadn't been seen for two days - two were deceased on beds and third was lying semi-conscious on floor; according to fire marshall in charge of investigation, "the exhaust from the gas space heater did not terminate on the exterior of the building...fumes from the heater vented into the attic above the room" "as submitted in the building plan, the whole motel unit was to have used hot water heat. At some point, however, gas space heaters were installed in the three upper rooms when it was determined that hot water would not heat the rooms sufficiently"; several weeks earlier a 21-year-old man was found unconscious in adjacent room but was thought to be associated with "an unusual strain of virus"
30 | TX | Odessa | 1972-12-08 | Randall Earl Hoover, 34 (deceased) | Sunset Motel |  | 1 |  |  | heater | room | victim found by hotel maid when she went to clean room; "open gas heater was located near the bed"
31 | NV | Reno | 1973-02-06 |  | Riverside Hotel |  |  | 20 |  | boiler |  | guests ill, casino dealers started collapsing around 10pm - fire dept called at 11:19pm and evacuated hotel; policeman found unconscious on 2nd floor while helping w/evacuation; investigators discovered "leak in boiler room, filtering unnoticed into the casino and parts of the hotel"
32 | AZ | Flagstaff | 1973-02-13 | Clarence C. Bowen, 22, (deceased), David S. Buchanan, 21 (deceased) | Skyline Motel |  | 2 |  |  | wall heater | room | victims discovered by maid when she went to clean the room; one victim found on a bed, the other on the floor
33 | IL | Springfield | 1973-05-30 |  | St. Nicholas Hotel |  |  | 37 |  | furnace | basement | "a fan in the hotel boiler room ceased functioning" allowing carbon monoxide to seep into banquet room which was being used for a conference; people began collapsing, originally suspecting they were suffering from food poisoning; among those injured were three policeman who were helping to evacuate the banquet room
34 | KY | Corbin | 1973-05-31 | Bertrand Devaux 22 (deceased), Richard Porch, 31 (injured), William Yule, 61 (injured) & wife, 51 (injured - name not listed), John Cozine, 50 (injured), Julian Hexter, 50 (injured), Gret Witters, 25 (injured) | Howard Johnson | Y | 1 | 6 |  | pool heater |  | ambulance called at 1am for a guest who was treated and released and returned to room; other ambulances were called for other guests and at 5:45am police were called to hotel to investigate - deceased victim found in room 201 while police were evacuating hotel; CO level measured at 270 ppm in room, high levels found in other second floor rooms; "gas originated from pump room where the count was 1000ppm. From here, it filtered into the ventilating system and into the rooms"; State Board of Health report stated possible source to be an improperly vented heater used to heat the swimming pool; a guest staying in room 201 the night before was ill and taken by ambulance to the hospital but treated and released after 30 minutes - returned to the room and passed out again, had planned to stay a second night but decided to go home
35 | AR | Hampton | 1973-12-08 | Ione Schadey, 51 (deceased) & husband Clarence M. Schadey, 65 (injured) | Word's Motel |  | 1 | 1 |  | heater | room | victims discovered by hotel owner when they failed to check out
36 | IL | Chicago | 1973-12-10 | Anthony Johnson, 60, Edward Schwartz, 70, Lee Hoagland, 52, S. Davidson, 50 (all deceased) | Hartman Hotel |  | 4 | 10 |  | water heater |  | victims found in rooms on the second and third floors; gas furnace and water heater vented into common chimney which had become blocked and caused fumes to fill building
37 | FL | Tampa | 1973-12-24 | Yvonne Ragsdale, 16 (deceased), John D. Tyler, 25 (deceased), Robert D. Kledhaus, 24 (deceased) | E and L Motel |  | 3 |  | 1 deceased | heater or stove | room | victims discovered deceased in room by manager, investigators estimated they had been dead for 24-48 hours
38 | CA | Trinidad | 1974-02-22 | Jeffrey Allen Carnahan, 18 (deceased) | Decker's Fireside Lodge |  | 1 |  | 1 deceased | heater | room | victim discovered deceased in room by a friend and the owner of the motel, time of death determined to be 5-6 days prior; investigation showed cause to be an improperly installed and improperly calibrated propane gas heater; prior occupants of room experienced nausea, headaches and fainting and had complained to the owner of the lodge; following a coroner's inquest the victims parents were quoted "We just wanted the public to know about this. A student comes up here and has a right to turn the heater on in his room and have it be safe. We just wanted people to know what was going on so Jeff won't have died in vain."
39 | IA | Okoboji | 1974-05-22 | Walker A. Johnston, 78 (deceased) & wife Neva Johnston, 76 (deceased) | Lakeshore Motel |  | 2 |  |  |  | room | victims discovered deceased in room by hotel owner who had not seen them since the prior day; room contained a gas range, gas space heater and a gas refrigerator (confirmed source of CO not listed); the couple's dog was found alive in the room but "very sick"
40 | NY | South Cairo | 1974-11-22 | William Cassell, 20, Robert Gagbeille, 27, Martha Nally, 18 (all deceased) | Greystone Motel |  | 3 |  | 1 deceased | space heater | room | victims discovered deceased by motel owner when they failed to check out; police investigation discovered malfunction of space heater provided by motel
41 | NM | Cloudcroft | 1975-01-04 | Pauline Frazier, 26 (deceased) & husband Donald Frazier (injured) & son Rickie Frazier, 2 (injured) | Spruce Cabins |  | 1 | 2 | 1 injured | heater | room | victims checked into motel late in the afternoon and at approximately 8pm the husband went to motel office to ask if there was a doctor because wife was ill - hotel staff advised him to take her to the emergency room; at 11:20am the following morning the manager went to room because they had not checked out, husband collapsed after answering door; wife deceased on bed; two other couples had reported being ill in the room prior to family checking in
42 | TX | Tulio | 1975-02-01 | Ethel J. Johnson, 34 (deceased) & William Wigfall, 34 (deceased) | Hillcrest Motel |  | 2 |  |  | heater | room | victims discovered deceased in room around 9:45am by maid after friends knocked on door and got no response
43 | AR | Calico Rock | 1975-02-08 | Sharon Hansard Tyrer, 21 (deceased), Annetta Reddman, 26 (injured) | White River Motel |  | 1 | 1 |  | heater |  | victims discovered by motel manager after housekeepers got no answer to knock at door
44 | IL | Decatur | 1975-11-13 | Debra Kidd, 22 (deceased) | Decatur Hotel |  | 1 |  |  |  |  | death originally investigated by police as an overdose, investigation re-opened when autopsy report did not agree with police investigation; subsequent investigation found a "faulty flue" - hotel had repaired the flue 3 days after the woman's death
45 | CA | Santa Maria | 1975-12-27 | Chad Kelsey, 2 (deceased) & mother Cheryl Kelsey, 19 (injured) | Western Motel |  | 1 | 1 | 1 deceased | heater | room | child discovered deceased in hotel room, mother unconscious
46 | MO | Joplin | 1976-06-08 |  | Ramada Inn | Y |  | 9 |  | pool heater | below victims' rooms | on 6/8 ambulances called for ill victims in rooms 125 and 225; a responding police officer remembered that the two rooms had been involved in prior ambulance calls and notified the Health Dept who immediately closed the rooms and began investigation; discovered the rooms were directly above the pool heater; prior incidents of ill guests being taken to the hospital on 4/30, 5/9, 5/18, 5/19, 6/4 - all occurred between 4 and 6am; hotel manager said he was aware of several of the incidents but did not relate incidents to a common cause, some told him they thought they had food poisoning; "The investigation showed that natural gas was not burning properly in the pool heater and was giving off carbon monoxide"
47 | TX | Del Rio | 1976-11-14 | Willie Lee Isaac, 22 (deceased) | Palm Courts Motel |  | 1 |  |  |  |  | victim checked into room around 8:30pm Friday, discovered deceased on floor of room by motel owner at 5:45pm Sunday; investigating officers reported "the victim's room was filled with soot halfway up the walls"
48 | GA | Jeffersonville | 1976-11-16 | Henry Lee Navarre, 46 (deceased), James Cecil Foster, 50 (deceased) |  |  | 2 |  |  | heating system |  | victims were discovered by coworker who went to wake them for work
49 | TX | Harlingen | 1977-01-31 | Michael Wysong, 40 (injured) | Little Creek Hotel |  |  | 1 |  | heater | room | victim found by hotel maid 17 hours after checking in; transported to hospital in comatose state where doctors diagnosed CO poisoning
50 | NM | Espanola | 1977-03-29 | Peter Begay, 59 (deceased) | Livingston Hotel |  | 1 |  |  | space heater | room | victim found dead in room the morning after checking in; death caused by CO leaking from disconnected exhaust vent attached to gas space heater in room
51 | FL | Miami Beach | 1977-05-24 |  | Montmartre Hotel |  |  | 43 |  |  |  | guests began feeling ill on Sunday but attributed symptoms to illness, most were at hotel attending a Red Cross convention - two days later began to be investigated as an environmental cause; guests were all staying in north wing of hotel; conflicting reports in news stories as to source of CO
52 | NV | Las Vegas | 1977-07-15 | Frank Gulla, 55 (deceased) | Landmark Hotel-Casino |  | 1 | 138 |  | auxiliary power generator | basement | auxiliary power generator turned on which produced CO and carried it throughout 31 stories of hotel via air conditioning vents; auxiliary generator came on when "a leaky pipe poured two feet of water into a sub-basement, drowning out an electrical control panel and knocking out the regular power supply"; originally investigated as a refrigerant gas leak until treating physicians diagnosed CO poisoning in victims; many of the hotel guests were attending a Disabled American Veterans convention; estimated 1000 guests evacuated; injured victims included guests, hotel workers and fireman; evacuation slow due to only one elevator operating; 31-story hotel
53 | KY | Lebanon | 1977-10-20 | James Robert Smith, 42, & wife Pauline Jeffers Smith, 28 (both deceased) | Holly Hill Motel |  | 2 |  |  | gas stove | room | couple had moved one week earlier from Texas and had no permanent address - last seen 4 days earlier; fire marshall found ventilation problems in the gas heating stove in the room
54 | IA | Clive | 1978-02-21 | Jerry Tripp, 48, Helen Owens, 52, Marlene Debruyn, Mary Lance, 50, Steve Fuller, 28, Ruth Medici, 47, Kay Laverty, 35, John Llewellyn, 40 (all injured) | Sheraton | Y |  | 8 |  | furnace |  | victims were attending meeting in large first floor conference room of hotel, sick and some semi-conscious when fire dept arrived; high levels of carbon monoxide found; fire dept discovered malfunctioning furnace
55 | MO | Springfield | 1978-05-28 | Milan L., 44 (deceased) & wife Florence Lincoln, 44 (injured); Ben Yates, 88 (deceased - father of Florence Lincoln) | Ship and Anchor Motel |  | 2 | 16 |  | water heater |  | Police notified by hospital that two guests of motel had been admitted with symptoms of CO poisoning about 6am, hotel was then evacuated; 88 y/o man and his son-in-law found deceased; CO traveled thru ducts of hotel from broken/disconnected pipe; lawsuit subsequently filed alleging plumbing company installed water heater incorrectly, city did not inspect the unit, and owners of hotel did not make sure the water heater was working properly
56 | CO | Estes Park | 1978-05-28 | Margaret Arnot, 27 (injured), Ester Maria Montoya, 36 (injured) |  |  |  | 2 |  | charcoal grill | room | victims built charcoal fire in room to cook hamburgers, then put grill in bathroom to burn out overnight - CO seeped under door; hotel staff alerted when one of the victims called for help after discovering her friend unconscious
57 | SD | Rapid City | 1978-07-22 | Frank McCune (injured) & wife Judith (injured) & 5 kids ages 8-15 (all injured) | Sands Motel |  |  | 7 | 5 injured | water heater | directly below victims' room | Victims all woke up ill in the morning feeling groggy and nauseated, Fire Dept was called to investigate; Fire Marshal said "a defective ventilator to hot water heaters combined with poor ventilation in the boiler room and ceiling penetrations cause the fumes to back up and enter the bedroom above."
58 | CO | Colorado Springs | 1978-12-22 | Lloyd Michael Breitman, 22 (deceased) | The Casa Motel |  | 1
59 | FL | Lakeland | 1979-01-13 | Henry Hoagland (deceased) | Cozy Court Motel |  | 1 |  |  |  |  | victim found dead in room by hotel manager after no response to multiple phone calls
60 | WI | Mauston | 1979-01-16 | Susan Gilbert, 19 (deceased), Julianne Larsen, 20 (injured), Nina Hansohn, 20 (injured) | Towne Inn Motel |  | 1 | 2 |  | space heater | room | victims found unconscious in their room by police officer looking to notify them that their car was illegally parked; "space heater's intake and exhaust were clogged with ice formations which resulted in carbon monoxide flowing into the room. This also resulted in part from the eroded condition of metal sleeves through which carbon monoxide was discharged outside. The eroded sleeves permitted the carbon monoxide to escape through the concrete block walls to the ceiling and back into the room."
61 | AZ | Tucson | 1979-01-27 | 24-year-old man (deceased) | Close-Inn Motel |  | 1 |  |  | heater |  | Fire dept investigation found high concentration of CO in victim's room as well as mulitple gas leaks in the heating system; owner quoted as saying he will have to tear hotel down because he cannot afford to make the necessary repairs to the pipes; many of motel's residents were long term tenants
62 | AZ | Tucson | 1979-02-05 |  | Paradise Inn Motel | [6 empty] | gas company shut off gas service to hotel "because of numerous gas leaks" found by the fire dept during an inspection ordered by city manager following death of man at nearby hotel (see case above #1979-0205AZ); most of the guests are long term residents
63 | AZ | Tucson | 1979-02-08 |  | Copper Court Motel | [6 empty] | gas company shut off gas service to hotel "because of numerous gas leaks" found by the fire dept during an inspection ordered by city manager following death of man at nearby hotel (see case above #1979-0205AZ)
64 | TX | Fort Stockton | 1979-11-03 | Johnny Ramos, 28 (deceased) | Gateway Lodge |  | 1 |  |  | wall heater | room | victim discovered deceased in bed by maid - she had opened the door the two previous days and saw the man's body in bed but thought he was sleeping, time of death determined to be three days prior
65 | TX | Odessa | 1980-01-12 | Joseph Earl Wynne, Jr., 28 (deceased) | Circle R Motel |  | 1 |  |  | wall heater | room | victim found by motel employee, deceased lying on floor of room at approximately 11:50am, time of death approximated at 1am
66 | IL | DeKalb | 1980-11-28 | Michael McGrath, 28 (deceased) | Rice Hotel |  | 1 |  |  | water heater | basement | CO leaked into victim's room 2 floors above basement; found 9 days after he checked in; no CO found when body was discovered but pink discoloration of hands prompted blood test which confirmed CO poisoning; "The date of death was probably Nov. 20…because (victim) checked into the hotel on the 19th, and Northern Illinois gas shut off the gas to the building Nov. 21 when hotel manager reported a gas leak"; CO "traveled through a hole around hot water pipes running from the basement to a radiator in his bedroom two floors above"
67 | TX | Odessa | 1980-12-12 | Richard Wayne Fletcher, 23 & Patti Marie Breckenridge (both deceased) | Traveler's Lodge |  | 2 |  |  | wall heater | room | victim's employer called manager of hotel when victim failed to show up to work or answer phone, manager subsequently discovered both victims dead in bed
68 | TX | Brownsville | 1980-12-23 | Patricia, 22 & husband Tom Navratil, 29, & their children, Amanda, 7 months (deceased), two other children, aged 2 and 4 (injured) | Del Mar Motel |  | 1 | 4 | 1 deceased 2 injured | stove | room | friend of family and hotel maid climbed in thru window when no response at door, discovered entire family unconscious; victims reported turning on the burners on the gas stove to keep warm when room heater did not provide enough heat
69 | MA | Newton | 1981-01-22 |  | Holiday Inn | Y |  | 24 |  | water heater |  | "Boston Gas Co. officials suspect the poisonous fumes escaped from an improperly installed flue on a hot water heater." approximately 100 people were evacuated from the affected meeting room
70 | AL | Montgomery | 1981-03-05 | Alonzo Bradford, 1 (deceased) & mother Mary Bradford, 18 (injured), Robert Lee Moore, 34 (injured - companion of Mary Bradford) | St. Francis Hotel Courts |  | 1 | 2 | 1 deceased 1 injured | heater | room | Family found by hotel maid; little boy found on floor, his mother on bed, man on bathroom floor
71 | OH | Brook Park | 1981-06-18 | Robert Weaver, 29 (deceased) | Sheraton Airport Hotel | Y | 1 |  |  | pool heater |  | victim discovered by maid, "the heater for the swimming pool, the previous year when they closed it up for the winter, someone put a piece of plywood there, and all the fumes came up into his room"
72 | FL | Bradenton | 1981-07-22 | Ronnie Cornelius, 33 (injured) & wife Connie Cornelius, 28 (injured) & sons Eddie, 3 (injured) and Daniel, 9 (injured), & neice Celeste Jokins, 11 (injured) | Holiday Inn | Y |  | 5 | 3 injured | charcoal grill | room | Family found unconscious in room by police who came to hotel after hotel clerk reported room was paid for using a stolen check connected to a purse-snatching incident a week earlier; father found sprawled on bed and rest of family on floor of room; parents were later charged with lighting fire in the grill in an attempt to kill themselves and the children.
73 | SC | Orangeburg | 1982-01-01 | Willie Harvey Brown III, 22 (deceased) | Carolina Wren Motel |  | 1 |  |  |  |  | Victim found deceased in room
74 | TX | Odessa | 1982-05-30 | Bernice Connery, 27 (deceased), Wayne Howard, 22 (injured), Danny Helms, 16 (injured), Ona Cargal, 16 (injured); also injured (no ages listed) were Leaetta Lawson & child Jarret Vaden, Sandra Thompson, Shirley Miller, Jerry Yoesting, Randal Crabtree (child), Joey Carlson, Billy Brannum (child), Gigi Dougan, Danny Helms (child) | Imperial Motel |  | 1 | 13 | 6 injured | water heater |  | Victims Connery and Howard treated for what was thought to be food poisoning in emergency room on May 29; police responded to call on May 30 and found Connery dead and Howard unconscious - three hours later they received another call that three more guests were found unconscious and subsequently found 11 more victims in various rooms; CO came from "a hot water heater vent pipe placed against a grating and not extended to the outside of the building"; Fire Marshal reported that two water heaters were inspected the prior December and one of the two was listed as a fire hazard due to no venting but inspector did not notice that the other heater was vented improperly; when the inspector returned on May 26 owners reported the heater with no ventilation was not in use - however, the heater with the faulty ventilation continued to operate due to the oversight; during investigation following the death city officials discovered the heater with the faulty ventilation was installed without a permit and had never been inspected; following incident, fire inspectors made plan to check every motel in Odessa
75 | FL | Lakeland | 1982-12-21 | Freddie S. Jones, 21 (deceased), Patricia Cromartie, 25 (injured) | Cozy Corner Motel |  | 1 | 1 |  | heater | room | Victims discovered in room by motel manager, man was on bed and woman on floor; investigators found vent pipe disconnected from heater and theorized it had been that way for some time as there was staining on the curtain behind it
76 | IA | Tipton | 1982-12-30 | Lanny Machovec, 34 (deceased), Bonnie Nielsen (injured) | Best Western Liberty Inn Motel | Y | 1 | 1 |  | fumes from smoldering insulation | adjoining room | Injured victim was in room below deceased victim's room; carbon monoxide came from smoldering insulation in ceiling of an adjoining room - resulting from short in heating system caused by leaky roof; CO entered victim's room via "holes left for installation of cables and wires in the fire wall" between his room and the adjoining room
77 | TX | Del Rio | 1983-12-30 | Orlando Gonzalez, 23 (deceased), Lydia Patino Cardona, 35 (deceased) | Palm Courts Motel |  | 2 |  |  | space heater | room | victims discovered deceased in room by motel manager; fire marshal found illegal space heater in victim's room and another room; investigator said "a few years back a man died at the motel with similar surrounding circumstances"
78 | PA | Edinboro | 1984-01-30 |  | Holiday Inn | Y |  | 27 | 25 injured |  |  | most of the victims were high school students attending a DECA convention; CO was found in rooms in a second floor wing of hotel; inspector with gas company theorized there was either a hole in the ventilation system or "the system wasn't ventilating high enough in the air"
79 | CA | San Jose | 1984-02-03 | Bae Seugn Hoon, 37 (deceased), Chea Song Pak, 37 (injured) | Wagon Wheel Motel |  | 1 |  |  | heater | room | victims discovered when they failed to check out of room; authorities thought they were suffering from food poisoning - cause/reason for death not discovered until another fatality in same room two days later - see case #1984-0205CA listed below
80 | CA | San Jose | 1984-02-05 | Dave Swafford, 30 (deceased) | Wagon Wheel Motel |  | 1 |  |  | heater | room | Victim discovered deceased in same room as another guest found two days prior - see case #1984-0203CA above; CO measured at 125ppm in room; another room in hotel also found to have faulty heater
81 | AZ | Tucson | 1984-02-10 | Debora Deluca, 26 (deceased), & daughter Jolene Deluca, 4 (injured), Bernard Franklin Winnie, 46 (injured) | Pine Wood Motel |  | 1 | 2 | 1 injured | heater | room | friends alerted hotel staff when the three failed to answer door; found mother deceased and her child and boyfriend semi-conscious; gas company found CO leaking from improperly vented gas heater
82 | CA | Hollywood | 1984-07-12 |  | Ramada Inn | Y |  | 34 |  |  |  | paramedics responded to hotel for sick person, called back for a second sick person and noticed a gas odor so called for additional units; hotel evacuated; CO dispersed throughout hotel thru air conditioning vents; CO levels at 200ppm
83 | NM | Albuquerque | 1984-12-22 | Don T. Wilson, 31 (deceased) | Nob Hill Motel |  | 1 |  |  | heater |  | subsequent lawsuit filed on behalf of victim alleged that boiler service owner failed to properly install and provide ventilation for a space heater as well as failed to inform the motel that he was not qualified nor licensed to install the heater
84 | NC | Winston-Salem | 1985-01-16 |  | Ramada Inn | Y |  | 30 |  |  |  | motel employees and some guests began losing consciousness in area around the kitchen around 7:30pm, hotel air checked for CO approximately 90 minutes later when doctors discovered high levels of CO in victims; injured included 13 firefighters and police who rushed in to help; guests were evacuated to an emergency shelter; a private engineering firm hired by the hotel "attempted to find a source for the carbon monoxide, which was found in heavy concentrations in some of the 30 people taken to hospitals. They theorized that carbon monoxide produced by the hotel furnace or by traffic on US 52 and nearby businesses became trapped near the ground and in the hotel lobby because of temperature differences between the ground and the layers of air above it. The carbon monoxide could then have been channeled into the hotel's ventilation system."
85 | MA | Boston | 1985-02-22 |  | Howard Johnson 57 Park Plaza Hotel | Y |  | 55 |  | water heater | 6th floor | "malfunction in the boiler allowed fumes to seep into sixth floor conference rooms"; 23-story hotel; hotel evacuated after guests began passing out from fumes; complaints from guests and meeting attendees that there was no evacuation plan and they were not informed of the reason for the evacuation, "switchboard operators were denying to callers seeking information that any problem existed or that an evacuation occurred"; two seperate conventions in process - approx 350 people attending a lawyers convention, one of the attorneys said the group had been discussing insurance coverage dealing with toxic materials
86 | NC | Statesville | 1985-03-12 | Emma Mae Lindsay (deceased) & son, James Lindsay III (injured) | US 21 Motel |  | 1 | 1 |  | heater |  | victims discovered by motel owner; referenced heater was "last manufactured in December of 1961"
87 | NV | Las Vegas | 1985-07-05 | Booker Anderson, 45 (deceased), Robert Shoemaker (deceased) | Crest Motel |  | 2 | 18 |  | water heater | 1st floor utility room | CO spread to one wing of the hotel; deceased victims were found in adjoining rooms near the water heater around 9:30am; some of the other victims were found unconscious; fire chief said "it appeared that the carbon monoxide had been building up for three or four days"; "City building inspectors said the water heater, which was installed without a permit since the motel was last inspected in April 1984, was larger than the unit it replaced and because of that was not proprely vented"; "A couple staying at the the motel said they were moved from room 137, where one of the dead people was found, two days earlier after becoming sick"; "The downtown motel rents rooms by both the day and week and houses some downtown hotel workers. Many of those staying at the motel were elderly tourists."
88 | TX | Amarillo | 1985-10-05 | Cornelius Hatten Jr., 24 (deceased), Tommy P. Barker (deceased) | The Sands Motel |  | 2 | 12 |  | generator |  | victims discovered by their employer around 8:30am when they failed to show up for work; employees said generator was being used after utility company cut off electricity to the motel due to unpaid bills; CO fumes from generator spread to other rooms; city inspectors condemned and closed motel after deaths
89 | KS | Lenexa | 1985-12-06 |  |  |  |  | 11 |  |  |  | hotel evacuated after CO fumes spread to north wing of motel
90 | VA | Troutville | 1986-01-14 | Susette Passionino-5 months pregnant, 21 (deceased) & fiance Anthony Storti, 31 (injured), Arthur B. LeBlanc, 46 (deceased) | Best Western Coachman Inn | Y | 2 | 8 |  | boiler |  | rescue workers dispatched to hotel at 7pm and again at 3am to treat guests complaining of breathing difficulties, did not immediately suspect CO; earlier around 5:30pm a hotel employee called boiler company because boiler was leaking (boiler company reported hotel told them repair could wait till morning); one of the injured guests remembered going to bed around 12:30am not feeling well and then woke up in an ambulance sometime later that morning; bodies of deceased victims were found at 4:30am by a janitor who saw water leaking from ceiling below deceased woman's room-she was found submerged in bathtub with water still running and her fiance was unconscious on hotel room floor; male decedent was found in adjacent room; CO cause determined to be due to high winds backdrafting fumes into hotel rooms due to an "obsolete" heating system that was 26 years old and did not meet current building code - inadequate chimney height and no exhaust fan on furnace
91 | NJ | Hackensack | 1986-01-19 | Jesse Davenport, 54 (deceased), Alvon Harrison, 23 (deceased) | Airport Motel |  | 2 |  |  | heater |  | victims found deceased in same room; deaths originally ruled as a heart attack and a cocaine overdose, a lawsuit filed two years later charged that their deaths were a result of a faulty heater based on the state medical examiner's toxicology report which showed that both victims "had many times the normal level of carbon monoxide in their blood at the time of death...enough to kill both of them"; after reading the news story about the lawsuit, the hotel's former maintenance man came forward and said the hotel owner had ordered him to repair the gas heater the day after the deaths
92 | NV | Wendover | 1986-08-19 |  | The Stateline Hotel and Casino |  |  | 30 |  | boiler |  | boiler had a bad seal and was directly under air conditioning duct causing CO to leak into air conditioning system; hotel evacuated; CO levels measured at 200ppm; victims reportedly included two pregnant women
93 | TN | Nashville | 1986-11-23 | John, 61 (deceased) & wife Joan, 67 (injured) Spaulding, Earl Shellum, 64 (injured), John, 63 (injured) & wife Frances, 65 (injured) Gleaves | Opryland Ramada Inn | Y | 1 | 5 |  | pool heater | adjacent to victims' rooms | victims discovered in their room around 12noon when man failed to show up at a convention meeting, he was deceased on floor and his wife sprawled on bed sick and disoriented; room to room search found several other disoriented guests who were taken to hospital; hotel not evacuated till 10pm when autopsy showed man died of CO poisoning; illness of other guests originally suspected as food poisoning; hotel was 18 months old and "the 308-room hotel was allowed to open with a temporary use and occupancy permit"; Health Dept Director said, "the design of the ventilation system for the swimming pool and the equipment room created a situation that caused carbon monoxide to build up in the pool equipment room and to filter into other rooms in the hotel...in addition, a gas water heater may have been defective"; this case was the subject of a JAMA article published in 1989, "Fatal Carbon Monoxide Poisoning at a Motel"
94 | MS | McComb | 1986-12-28 | Darrell D. Jones, 49 (deceased) | Economy Motel |  | 1 |  |  | heater | room | victim discovered deceased in room by motel staff; high levels of CO found in room; heater was found to have a defective vent; on autopsy, victim appeared to have died of a heart attack but due to CO found in room toxicology was ordered and 3 1/2 months later confirmed he had died of CO poisoning with a blood CO level of 43%
95 | HI | Wilea (Maui) | 1988-01-22 | Constancio Alviedo, 61 (deceased) | Maui Intercontinental Wailea Hotel |  | 1 | 9 |  | generator | basement | deceased victim was employee of hotel, discovered unconscious near trash compactor in basement - ambulance responded to "an apparent heart attack"; rescuers discovered two additional victims lying near first victim - three other employees collapsed in nearby employee locker room "prompting an evacuation of the area that includes a service tunnel, loading dock and the compactor room"; multiple first responders ill at scene - 4 required treatment at hospital; 20 minutes prior hotel had been testing the emergency generator - exhaust pipe was vented into the trash compactor room; according to police, "generator was run from about 1pm to 1:35pm...Alviedo was found unconscious at 1:52pm...exhaust vent is located near the doorway of the trash compactor room"
96 | AR | Mountain View | 1988-01-24 | Mary Umpleby, 36 (injured) & granddaughter Chastity Wilson, 2 (deceased), & son Garrett Long, 14 (deceased) & friend James Robin, 25 (injured) | Mountain View Motel |  | 2 |  | 2 deceased | heater |  | Medical Examiner determined cause of death to be CO poisoning by gas heater in the room; Director of LP Gas Board said an inspector "tested the heater twice…did not find it to be operating improperly"; a state police investigator considered the case closed and was "satisfied there was no foul play...tests by an inspector for the state LP Gas Board don't mean there was nothing wrong with the heater at the time of the deaths"
97 | FL | Miami Beach | 1988-04-06 |  | Fontana Hotel |  |  | 42 |  | boiler |  | CO spread thru air conditioning system; rescuers called to hotel for guest who had passed out and found many others complaining of CO symptoms; CO levels measured at "300 times what is considered normal"
98 | CA | Hayward | 1988-11-06 | Michael Horvath, 33 (deceased) & fiancee Gloria Burroughs, 34 (deceased) |  |  | 2 |  |  | water heater
99 | MT | Saltese | 1988-11-23 | Bruce, 28 & Colleen, 29 MacMaster (both deceased) | 4-D's Motel |  | 2 |  |  | heater | room | heater found to be improperly vented; "heater should have been vented up a chimney instead of horizontally out a wall"; heater had been installed by hotel owners without a permit; investigation found that other people who had stayed in the same room prior to incident had also been ill
100 | AZ | Mesa | 1989-02-08 | Family of 4: Al Stjernberg 26, Sandra Magness 25, & daughters Amanda 18 months and Jessica, 8 months (all deceased) | Florian Motel |  | 4 |  | 2 deceased | 1950's-era gas heater |  | employee found bodies of family along with their dead German shepherd; fire dept found room's heater not connected to a chimney; motel built in 1933
101 | CT | Windsor Locks | 1989-10-31 | Sharon Matos, 33 (injured) | Motel 6 | Y |  | 1 |  | dryers | laundry room | hotel opened 9 weeks earlier; victim was employee of motel, began feeling dizzy and collapsed in laundry room; on 10/25 two other workers were taken to the hospital after becoming ill in the same room - hotel owners called gas company after incident but gas company did not detect CO or other gases; one of the two workers went to the hospital again two days later and was found to have elevated CO levels in blood; OSHA inspector responded after employees filed complaint; on 11/1 town building inspector detected CO in laundry room and engineers determined "that a down draft caused by low-flying airplanes was probably forcing exhaust containing the poisonous gas back down the flue into the room"; hotel subsequently installed fans in the exhaust pipes of the two dryers in the laundry room
102 | SD | Rapid City | 1989-11-18 | Steven Beach, 38 (deceased) | Dakota Motel |  | 1 |  |  | furnace |  | victims discovered deceased in rooms a day apart in rooms 122 and 126; CO not suspected with first victim because according to coroner he "didn't show the classic signs" of CO poisoning and death was ruled as natural; investigation ordered when second man was discovered deceased the following day; a woman in room 121 had complained of nausea and "an odd odor" in her room; investigation showed CO came from a single gas furnace that supplied heat to rooms 121-126; motel was 30 years old and had never been inspected; CO exposure thought to be a result of "back drafting" - motel manager re-lit pilot light when victim Russell complained of being cold but neglected to replace the front panels of the furnace - "exhaust gases could have been pulled from the system back into the cold air return on the bottom of the furnace, poisoning the air in the rooms"
103 | SD | Rapid City | 1989-11-19 | Eugene Thomas Russell, 25 (deceased) | Dakota Motel |  | 1 |  |  | furnace
104 | OH | Fairlawn | 1990-01-04 |  | Days Inn | Y | [5 empty] | firefighters called to motel when fumes set off an alarm - natural gas was shut off and hotel closed until source of CO could be determined
105 | IN | Evansville | 1990-01-25 |  | Radisson Inn | Y |  | 14 |  |  |  | group of conventioneers began feeling ill; county health officials could find no problem; highest level of co found in patients was 32%; victims all in wing of 16 rooms on 1st floor "where inside windows overlook an enclosed area with a swimming pool"
106 | KY | Jefferson County | 1990-02-03 |  | Brownsboro Inn |  |  | 34 |  | boiler |  | two of three wings of hotel evacuated after guests awakened feeling ill around 7am; 34 guests transported to nine hospitals; investigation found broken boiler not properly reassemled by the repair crew that had worked on it earlier in the week - stack was loose as well as a 3/4" crack in the front of the boiler; stack was disassembled by workers who took the boiler apart to repair an unrelated problem
107 | CA | Fallbrook | 1990-04-07 |  | La Estancia Inn |  |  | 20 |  | propane-powered cogeneration unit |  | Some hotel guests felt ill but assumed food poisoning in the evening, hotel manager called for ambulance when guests continued to complain of feeling nauseous the next morning; 8 of the victims treated in hyperbaric chamber; 12 firefighters, 1 police officer and other guests were hospitalized
108 | MI | Watersmeet | 1990-06-16 | David & Debra Pilipauskas, William Pilipauskas, Sandra & Matthew Rusek (all injured) | Arrow Lodge Resort
109 | MN | Spicer | 1990-07-01 |  | Cazador Inn |  |  | 120 |  | pool heater |  | EMS called around 8am for a guest who was sick, when they arrived discovered multiple people ill, some unconscious; firefighters did "room by room sweep"; fire depts and ambulance crews from five neighboring towns were called in to help, local hospital called in 50-60 additional personnel; hotel employees had been ill with headaches and dizziness in days prior; injured included guests, firefighters and employees; subsequent investigation found swallows' nests clogging pool heater vent
110 | MI | Lansing | 1990-09-18 | Michael Daugherty, 20 (injured), Daniel Crow (injured), Jarrett Pearson, 17 (injured) | Ramada Inn | Y |  | 3 | 1 injured | pool heater | room next to pool | motel workers found two of the victims unconscious in the pool area; faulty pool heater vent stack leaked carbon monoxide through louvers in a door adjoining the pool
111 | CO | Silverthorne | ?/?/1990 |  | Silverthorne Comfort Inn | Y |  |  |  | pool heater |  | swimming pool boiler vent system failure; hospitalization of hotel guests
112 | CO | Pueblo | ?/?/1990 | [8 empty] | *listed on Dr. Weaver's spreadsheet, source listed as Colorado Springs Gazette - unable to find further information online
113 | CA | San Diego | 1991-01-01 | Cory Korosi (deceased), 21, Henry Kim Wong (injured), 20 | Mission Valley Inn |  | 1 | 1 |  | wall heater | room | victims were discovered about 2:30pm after friends could not get answer at door, contacted hotel security who broke a window to gain entry to room; building inspector said heater in room appeared to be original to the building which was constructed in early 1960s; venting system also clogged with soot so natural gas heater was working poorly; following the incident, the Building Inspection Dept found violations in 83 of the 190 rooms inspected, including malfunctioning heaters in 36 of the rooms; victims were members of the Southern Alberta Institute of Technology's men's volleyball team in town to play four exhibition games; Chairman of the city's Public Services and Safety Committee, "It's tragically been brought to our attention. I'd like to see how the Hotel-Motel Assn. could assure the city and public that there are hotels and motels that are not only beautiful, but safe."; city building inspectors and the San Diego County Hotel & Motel Association reported they would jointly send out letters to all county hotels and motels to remind owners and operators of "the obligation to properly maintain all mechanical equipment"
114 | WI | Stevens Point | 1991-11-08 |  | Comfort Suites | Y |  | 72 |  | pool heater |  | victims reported feeling nauseous and dizzy after spending time in the pool area; CO leaked from improperly installed ventilation system, CO levels at 450ppm
115 | FL | West Palm Beach | 1992-03-21 | Todd Girouard, 21, Kimberly Newton, 21, Kirsten Madden, 20 (all injured) | Holiday Inn - Airport | Y |  | 4 |  | boiler | second floor (below victims' room) | victims discovered around 3pm by hotel staff; "It is not clear how long the three were exposed to fumes from the hotel's gas-fired boiler…by the time the housekeeper discovered them and called for help, the gas had spread to three floors"; hotel employee collapsed while inspecting the boiler room; CO levels were measured at 210ppm on the second floor; a state fire investigator "determined that leaks and closed vents in a hotel boiler system produced high levels of carbon monoxide…maintenance workers knew about leaks and tried to seal pipes with duct tape"; "Gas apparently leaked into a third-floor room...through an exhaust duct connected to four boilers on the floor below. Two pipes carrying cold water to air conditioners in the students' room ran through the duct. Leaks around the pipes allowed the gas to seep through"; "Vents allowing air into the boilers were closed, which caused the water heaters to produce exhaust rich in carbon monoxide instead of air"
116 | TN | Knoxville | 1992-05-14 |  | Family Inn |  |  | 10 |  | water heater |  | CO found in 24 rooms; improperly installed laundry room fan cause CO from water heater to disperse into rooms;
117 | CA | Indian Wells | 1992-12-12 |  | Stouffer Esmeralda Resort |  |  | 8 |  | heater |  | multiple calls to 911 by guests feeling ill beginning at 6:21am; fire dept evacuated hotel and discovered malfunctioning heater
118 | NC | Durham | ?/?/1992 |  | Cricket Inn | [6 empty] | *listed on Dr. Weaver's spreadsheet, source listed as News & Observer - unable to find further information online
119 | MA | Boston | 1993-02-07 |  | Back Bay Hilton | Y |  | 6 |  | boiler | basement | problem identified when "hotel maintenance workers were in the basement...trying to correct a water temperature problem after a guest's complaint when they began to complain of nausea and headaches. Fire officials were then called in and discovered the build-up of carbon monoxide"; 25-story hotel evacuated; victims hospitalized included hotel employees who tried to fix leak; "officials said the bitterly cold weather probably caused the boiler to back up with carbon monoxide"
120 | TN | Nashville | 1993-03-24 |  | Doubletree Hotel | Y |  | 16 |  | boiler |  | outside air ducts were blocked and employees had propped open doors to boiler room, large ventilation fans had been turned on in the adjoining room which created a vacuum pulling the boiler exhaust back down the pipe and into the hotel; "system is similar to the systems in most large buildings in Nashville, but some have an added safety device. For the last five years, boiler systems have been built with sensors which automatically shut down the system if they detect carbon monoxide. The Doubletree, built in 1979, does not have such a system."
121 | TX | Arlington | 1993-03-27 | Edward Burner Anderson, 54 (deceased) | Days Inn | Y | 1 | 40 | 1 injured | water heater | room next to deceased victim's room | Fire Dept called to hotel multiple times beginning at 3:40am by guests ill with severe headaches and stomach upset, eventually discovered high levels of CO throughout hotel and evacuated rooms via door to door notification of guests; Fire Dept spokesman reported CO poisoning was not originally suspected because patient "did not have the rosy complexion that often accompanies the ailment"; CO levels measured at 500ppm; deceased victim unable to evacuate and was discovered deceased on bathroom floor of his room by city health inspector 5 hours later (subsequent formal inquiry/report regarding evacuation procedure was completed by Fire Dept and reviewed by city officials); guests not informed of why they were being told to evacuate; CO leaked from "ruptured" water heater vent pipe that had been patched with duct tape; new water heater installed without city permit
122 | IN | Evansville | 1993-09-07 |  | Executive Inn |  |  | 2 |  | carpet cleaning equipment |  | hotel evacuated; worker whose office was located in basement was hospitalized; "fumes escaped while a (carpet cleaning crew) operated steam-cleaning equipment in a first-floor ballroom…machinery was powered by a gasoline engine on a truck parked in a hotel loading bay, and exhaust fumes backed up after a hose connecting the cleaning equipment and the truck became obstructed"
123 | UT | Salt Lake City | 1993-12-10 | Samual Doan, 83, and Madalyn Jereb, 53 (both deceased) | Holiday Motel |  | 2 |  |  | heater | room | police called to hotel after receiving reports of "an usual odor" and discovered victims, appeared to have been dead for some time, checked in six days prior; man found on floor near bed and woman lying back in chair
124 | AZ | Mesa | 1994-01-09 | Geraldine Tate, 62 & Cecil Constable, 77 (both injured) | Starlight Motel |  |  | 2 |  | heater | room | couple woke up with headaches and breathing problems and called 911; fire dept detected "potentially lethal levels of carbon monoxide" in the room
125 | IA | Mason City | 1994-02-26 | Donald Easton, 68 and Michiko Walton, 53 (both deceased) | Colonial Inn |  | 2 |  |  | furnace |  | victims were owners of the motel and lived onsite, found in living quarters adjacent to motel office; man found on bed, woman on floor; no guests staying at motel during evening of incident; authorities found no defects found in gas furnace but theorized high winds and snow may have caused downdraft that trapped CO in room
126 | IL | North Aurora | 1994-10-20 | Joanne Meister, 42 (injured) | Super 8 | Y |  | 10 |  | pool heater |  | motel guests complained of feeling ill, taken by ambulance to hospital where diagnosed with CO poisoning, hospital alerted fire dept who then evacuated motel; CO levels reached 400 ppm in some areas of hotel; firefighters obtained list of occupied rooms from hotel and evacuated all occupied rooms - list did not include Ms. Meister, she was found unconscious two hours later when firefighters performed room by room search; subsequent investigation determined "hotel maintenance workers walled off the boiler that heated the pool after fire inspectors cited the motel for having papers in the same room as the boiler. That caused the boiler to create carbon monoxide that seeped into the motel's ventilation system and into the bathroom vents on the same level as the boiler"
127 | MD | Ocean City | 1994-11-26 |  | Princess Royale Hotel |  |  | 24 |  | furnace | basement | around 6:30am a family of five at hotel called 911 thinking they had food poisoning, later other callers reported similar symptoms; emergency responders became ill as well; malfunction of one of three furnaces in basement, CO leaked into three rooms on second floor
128 | TX | Irving | ?/?/1994 |  | Red Roof Inn | Y | [5 empty] | *listed on Dr. Weaver's spreadsheet, source listed as Fort Worth Star Telegram - unable to find further information online
129 | FL | Tampa | 1995-02-02 | Ronald Blank, 51 (deceased), James Harold Ream, 37 (injured), Steve Kinder, 51 (injured) | Embassy Suites Hotel | Y | 1 | 2 |  | water heater | two floors below victims' room | Blank's friends asked hotel to check room when he did not show up, maid found him deceased and Ream unconscious in their room (317 - located on first floor of guest rooms); Kinder was in 417 directly above them and was found conscious but ill; fire dept measured CO levels of 250ppm in 317 and levels exceeding 400ppm in the boiler room where the water heater was located; leak was traced to a "small auxiliary water heater"; hotel manager reported they would install CO detectors immediately; several guests reported that they were not notified of the problem until "hours" after men were found and that only nearby rooms were evacuated; Blank and Ream both reportedly thought they were ill with the flu
130 | CA | Mammoth Lakes | 1995-02-10 | Walt Weber, 42 (deceased) & wife Molly Weber, 36 (injured) | North Village Inn |  | 1 | 1 |  | heater | room | victims checked in Friday evening, found unresponsive in room at 12:30pm on Sunday; "carbon monoxide was produced by a gravity-vented wall heater…manufactured in the late 1950s...the heater was allowed to operate with the heat exchanger detached from the draft diverter, causing the flue products to spill into the living area"; Molly's siser, Lyrysa Smith, published book about her recovery in 2013 "A Normal Life"
131 | VA | Virginia Beach | 1995-08-07 | Larry Corbett, 25 (injured) | Murphy's Emerald Isle Motel |  |  | 44 |  | furnace |  | "dangerous levels" of CO were found on the motel's top three floors
132 | CA | Sacramento | 1995-12-09 | Ferrel Bradbury, 79 (deceased) | Forty-Niner Motor Lodge |  | 1 | 1 |  | heater | room | man found dead in room; coroner investigation showed CO poisoning resulted from a "dirty heater"
133 | CO | Fort Collins | ?/?/1995 |  | Holiday Inn | Y | [5 empty] | *listed on Dr. Weaver's spreadsheet, source listed as Rocky Mountain News - unable to find further information online
134 | IL |  | ?/?/1996 |  | Budgetel Inn | [6 empty] | *listed on Dr. Weaver's spreadsheet, source listed as Lexis Nexis Legal - unable to find further information online
135 | KY | Danville | 1997-01-28 | Julieanne Boise, 30, Charles Baughman, 47, James Filipiak, 46, Chad Cooper, 26, Linda Schultz, 46, & daughter Jennifer Schultz, 17 (all injured) | Holiday Inn Express | Y |  | 6 | 1 injured | pool heater |  | CO escaped up thru a broken exhaust pipe for the pool heater and thru a ceiling opening around a pipe, then to exhaust vents of the hotel rooms' bathrooms, discovered when a frequent guest of the hotel did not respond to a wake up call and was found unconscious in room, two other guests came to front desk complaining of feeling faint; CO levels measured at 70ppm in lobby, "additional readings in hotel rooms were as high as 600ppm and above"
136 | CA | Daly City | 1997-02-20 | Clarence D. Brown, 46, Mildred K. Allen, 41, & daughter Talisha Brown, 2 (all deceased) | Alpine Motel |  | 3 |  | 1 deceased | heater | room | victims discovered deceased in room by maid - woman and child on bed, man on floor; investigators reported that vent for room heater was blocked but unable to determine for how long; heater removed for further testing; motel had minor health and safety violations - "inspectors check to see if heaters produce heat, but do not check the internal systems"; guests who stayed in room three days earlier had headaches and "found it difficult to wake up" while staying there
137 | MT | Somers | 1997-03-15 |  | Ramada Inn | Y |  | 8 |  | pool heater | room adjacent to hot tub | victims were in hot tub and began having headaches, nausea and weakness, one lost consciousness in hot tub and another went to call 911; CO found leaking from rusted out section of exhaust pipe, "fans designed to ventilate and expel humidity from the pool room then pulled in the deadly gas through the vents in the door separating the hot tub area from the boiler room"
138 | IA | Ottumwa | 1997-08-16 |  | Parkview Plaza |  |  | 4 |  |  |  | 4 members of family staying on top floor went to hospital complaining of headaches and dizziness; hospital alerted police and fire who found high CO levels on every floor and evacuated hotel
139 | TX | Arlington | ?/?/1997 |  | Arlington Hilton | Y | [5 empty] | *listed on Dr. Weaver's spreadsheet, source listed as Fort Worth Star Telegram - unable to find further information online
140 | IL | Peoria | ?/?/1997 |  | Mark Twain | [6 empty] | *listed on Dr. Weaver's spreadsheet, source listed as Journal Star - unable to find further information online
141 | FL | Fort Walton Beach | 1998-08-04 |  | Marina Bay Resort |  |  | 20 |  | boiler |  | family of four went to hospital complaining of headaches and nausea, doctors diagnosed CO poisoning and called fire dept; fire dept found other guests ill and evacuated hotel
142 | FL | Clearwater | 1998-09-09 | Kenneth Vaughan, 34 (injured) & wife Cheryl Vaughn, 32 (injured) | Quality Inn Beach Resort | Y |  | 3 |  | water heater | first floor | victims awoke feeling ill in the afternoon and called 911 thinking they had food poisoning but were disoriented; responders quickly determined they were suffering from CO poisoning and pulled fire alarm to evacuate hotel; other victim was a paramedic; Fire Chief reported "a clogged vent from a natural gas water heater on the first floor caused the problem. CO from the vent seeped out at the roof level and leaked into the Vaughans' room on the fifth floor....CO was also found in other areas of the hotel but highest level was in the area of the Vaughans' room;" CO levels measured at 180-200ppm
143 | VA | Virginia Beach | 1998-12-16 |  | Murphy's Emerald Isle Motel |  |  | 2 |  | boiler |  | prior incident at this hotel 8/7/1995 (see case above); authorities were called when "several boxes of carbon monoxide detectors in storage in the boiler room went off due to a faulty flue pipe in the boiler"; "…not clear whether the same furnace caused the problem in 1995"
144 | IA | Mason City | 1999-01-11 | Bruce & Bobbi Hollowell & their 2 children; Duane & Marjorie Dannen & their 3 children; Echo & Steve Cash; Terry & Jill Black & their 2 children; Debra Lugar & her 2 children | Comfort Inn | Y |  | 19 | 9 injured | pool heater |  | fire dept notified around 9pm when two children became ill and were diagnosed with CO poisoning at the hospital; multiple families ill with headaches and vomitting; fire dept evacuated hotel, measured CO levels at 668ppm in pool area; victim described event, "it was chaos"; CO found to be leaking from "faulty exhaust system"
145 | NY | Manhattan | 1999-07-03 |  | Crowne Plaza Hotel | Y |  | 11 | 1 injured | sandblasting machine | basement | CO spread to parking garage and lobby; 3 construction workers and an 11 y/o girl taken to hospital, 7 others treated at scene; sandblasting machine was being used to remove paint in basement of hotel
146 | MA | Yarmouth | 1999-10-06 |  | West Yarmouth Inn |  |  | 24 | 11 injured | clogged heating unit |  | CO leak discovered after family of 3 went to ER complaining of food poisoning around 8am - doctors diagnosed CO poisoning and alerted fire dept who found 8 other residents in "various states of distress, including an unconscious 3 year old"; injured victims included two pregnant women; CO found in 10 of hotel's 34 rooms; higher levels of poisoning found in those who had turned on heat in their room; incident led to discovery of multiple families (including 44 school-age children) living at that hotel and other hotels in the area because they could not afford to rent apartments
147 | IN | Merrillville | 2000-08-11 | Injured included: guests Joseph Topor, 48 & wife Amy, 27, hotel employees Roshanda Hinton, Nicola Sinclair, 34, Barbara Grubbs, 58 | Holiday Inn Express | Y |  | 24 | 15 injured | pool heater |  | children (ages 9-18) at a pool party became ill - two transported to hospital after collapsing about 9pm - but symptoms not connected to CO poisoning until hotel staff also became ill several hours later - front desk employee collapsed while working; first responders arrived and evacuated hotel via the fire alarm at 7:30am; CO readings in pool were over 1000 ppm; "When asked if the Holiday Inn would be installing carbon monoxide alarms (manager) said he would leave that to the experts, 'Whatever those experts tell us is the absolute right thing to do, this Holiday Inn is committed to doing the right thing...according to Holiday Inn, the state and local municipalities, we have everything required by code. Carbon monoxide detectors are not required"; subsequent lawsuit complaint stated "purpose of our request for punitive damages is to compel this chain, and every other hotel operator in Indiana, to install carbon monoxide detectors in all hotels before deaths or injuries occur."
148 | NY | Amsterdam | 2000-10-11 | Ursula & Richard Vasieck; Pentz family: Calvin & Marietta and their children Calvin Jr., 6, and Kristina, 10 (all injured) | Amsterdam Best Western | Y |  | 12 | 2 injured | pool heater |  | mother of family affected was awakened at 3am by the sound of a passing train and realized she was "violently sick", she woke up family members who were all feeling same effects - called front desk who called 911; firefighters evacuated hotel and found Vasieck couple - she was unconscious and he was semi-conscious; "Health Department investigators concluded that the heater had been improperly maintained, causing the carbon monoxide leak," - hotel fined $500; CO detection system was installed following incident
149 | CO | Denver | 2000-11-01 | Eric Potteiger, 30 (injured), Amy Bronn (injured) | La Quinta Inn | Y |  | 6 |  | pool heater | ground floor | housekeepers found unconscious guest on 2nd floor at 11:40am, firefighters responded and while there, housekeepers found another guest found unconscious on 3rd floor; firefighters did room by room search for more victims; around 4:30pm the cause of the CO was determined to be pool heater's exhaust system not operating properly; "A police report attached to the federal lawsuit quotes a hotel manager as saying that, while rescue authorities were responding, La Quinta's legal department told employees to deny any knowledge of any sick or ill people"
150 | TX | Georgetown | 2000-12-28 |  | Holiday Inn | Y |  | 4 |  | water heater |  | around 11:20 am, a victim called 911 after becoming ill with nausea and dizziness; CO leak detected by first responders who evacuated hotel
151 | IL | Effingham | 2001-02-16 |  | Lincoln Lodge Motel |  |  | 10 |  | furnace |  | 2 guests transported to hospital around 3:30am, doctors diagnosed CO poisoning and notified Fire Dept who returned to hotel at 4:41am and discovered eight additional victims who were taken to hospital; high levels of CO found in 5 rooms
152 | TX | Odessa | 2001-03-27 |  | Best Western Garden Oasis | Y |  | 1 |  |  |  | hotel employee ill and went to hospital; hospital diagnosed CO poisoning and notified the fire dept; "fatal levels" of CO found in areas of second floor, biggest accumulation was in a conference room; Asst Fire Chief, "it's unusual to find this much gas and only one person sick"
153 | WY | Teton Village | 2001-08-02 | David, 51 (deceased) & Joette Williams, 50 (injured) | Snake River Lodge & Spa |  | 1 |  |  | boiler | below victims' room | friends discovered both victims unconscious in their room in the morning, man died later same day at the hospital, woman flown to Pocatello, ID for treatment in hyperbaric chamber; victims had been taken to emergency room from hotel the day before with symptoms including nausea and diarrhea, treated for dehydration and then discharged, returned to hotel room; subsequent investigation found room CO levels at 770 ppm, "gases from the first-floor laundry room, which housed some of the hotel's dryers, water heaters and boiler units, were released through a vent....lint from the laundry room was plastered to air conditioning units in several rooms...room's air conditioning unit, which operated by sucking air in and cooling it, likely pulled in carbon monoxide gas after it was emitted from the laundry room"; a safety switch on a water boiler had been disabled - the switch which was to shut boiler off "if proper combustion did not occur" - switch disabled because it interfered with hot water production at the hotel; reports of both guests and employees suffering from similar symptoms prior to victims checking in; hotel installed CO detectors following incident
154 | NM | Moriarty | 2001-11-18 |  | Lariat Motel |  | 1 | 1 |  |  | room | 2 guests found in their room, one deceased and one unconscious, by motel workers around 10am when they failed to check out
155 | MA | Palmer | ?/?/2001 |  | Kings Inn | [6 empty] | *listed on Dr. Weaver's spreadsheet, source listed as Union-News Springfield - unable to find information online
156 | CA | Ventura | ?/?/2001 |  | Mission Bell Motel | [6 empty] | *listed on Dr. Weaver's spreadsheet, source listed as Ventura County Starr - unable to find information online
157 | NM | Carlsbad | 2002-07-06 |  | Park View Motel |  |  | 2 |  |  |  | two victims were women found unconscious in room
158 | WI | Chetek | 2002-08-21 | Frank Hekenberger, 81 & wife Catherine Hekenberger, 85 (both deceased) | Northland Resort |  | 2 |  |  | furnace |  | couple had stayed at resort many times previously; owner noticed he had not seen them and went to check on them around 12noon - found body of husband in the kitchen/living area and left to call 911; fire dept reported CO levels at 248 ppm and found corroded furnace vent pipe, clogged chimney
159 | NY | Albany | ?/?/2002 |  | Holiday Inn | [6 empty] | *listed on Dr. Weaver's spreadsheet, source listed as Times Union - unable to find further information online
160 | AZ | Flagstaff | 2003-01-08 | Jack Foster, 31 & Jeanette Laurer, 25 (injured) - she was 8 1/2 months pregnant and delivered stillborn baby after being transported to hospital | Paradise Motel |  | 1 | 2 | 1 deceased | wall heater | room | hotel owner knew the heater was broken and gave the couple an electric heater to use - husband thought he fixed the heater so turned it on; stillborn's death determined to be from CO poisoning
161 | KS | Salina | 2003-09-16 | Rivers family: Roslyn, 36, Robert 41, Adam, 10 and Alexis, 9 (all injured) | Holiday Inn Express | Y |  | 4 | 2 injured | pool heater |  | Family had been in pool for 15 minutes and all began feeling ill - all got out, boy passed out and fell in pool, father collapsed; fire dept responded and found CO levels of 1600ppm in pool room and faulty vent for pool heater; hotel installed CO alarms following incident
162 | MA | Danvers | 2003-09-17 |  | Sheraton Ferncroft Hotel & Resort | Y |  | 4 |  | pool heater |  | 4 victims were maintenance employees of hotel - 2 were found unconscious on the floor of the boiler room when they had been out of contact for an unusual amount of time; hotel evacuated, corrider outside of boiler room measured CO levels at 900 ppm, failure of pool heater vent system
163 | MO | St. Louis | 2003-12-18 |  | Chase Hotel |  |  | 2 |  | water heater | basement | fire dept called when 2 laundry room workers became ill around 11am; found elevated levels of CO in basement and evacuated guests
164 | NH | Lincoln | ?/?/2003 |  | Indian Head Resort | [6 empty] | *listed Dr. Weaver's spreadsheet, source listed as Union Leader - unable to find information online
165 | WY | Jackson | 2004-01-17 |  | 49'er Inn and Suites |  |  | 18 |  | boiler | below victims' rooms | three guests called front desk reporting rapid heart rate, dizziness and lightheadedness - hotel called 911; "Firefighters determined that the gas escaped from a broken connection in two pipes leading from the motel's boiler beneath the rooms where the victims were staying" - theorized that pipe may have been broken due to a 5.0 magnitude earthquake that hit area on January 7; Fire Dept measured CO levels at 300ppm in victims' room who had the most exposure - those victims were flown by helicopter to hospital in Pocatello, ID for treatment in a hyperbaric chamber; hotel installed CO detectors in "all areas of combustion" following incident
166 | AZ | Kingman | 2004-02-14 | Sharmallee Ann Johnson, 20 (deceased), and boyfriend Frederick Louis Herzer, 23 (injured) | Best Western Kings Inn | Y | 1 | 1 |  | boiler | below victims' room | Couple checked into suite on 2/13; at about 7pm on 2/14 "management found a deceased female in a bathtub and a male who was not responsive on a couch"; CO levels in room measured at 420ppm; surviving victim was flown to Barrow Neurological Institute in Phoenix in critical condition; "nickel sized holes in the boiler's exhaust pipe" were found; according to subsequent lawsuit filed, the installer of the jacuzzi tub in bathroom "failed to properly caulk or otherwise seal the holes...creating a common airspace between room 240 and the boiler room"
167 | IN | Indianapolis | 2004-06-09 | Robert Perreault (injured), Raymond Williams (injured) | Amerisuites | Y |  | 2 |  |  |  | Westlaw Perreault v. Prime Hospitality Group 2006; Raymond v. Prime Hospitality Group 2006; complaints state that both victims were guests at the hotel and suffered CO poisoning caused by CO seeping into their rooms
168 | NJ | Newark | 2004-07-07 |  | Best Western Newark Airport West | Y |  | 15 |  | transformer fire | in a small bldg about 6 ft from main hotel bldg as well as walls between rooms | hotel employees called 911 when guests complained of feeling faint - "shortly before the clatter of in-room carbon monoxide alrams signaled that something was wrong"; high levels of CO in upper floors; firefighters unable to find source, called HazMat team who found "elevated carbon monoxide levels from the vaporizing of PCB-laden insulation on the transformer's wires"; transformer located in a separate building - fumes spread thru hotel ventilation system, "more fumes were created when other electrical wires sizzled inside walls between the rooms"; six story hotel; hotel windows don't open so difficulty clearing building of CO
169 | SD | Yankton | 2004-12-23 | Eleshia Zahrbock, Peyton Gerry, Justin Zahrbock, Jonette Anson | Star Brite Inn Motel |  |  | 4 | 1 injured | furnace |  | man, woman and 5 y/o child experiencing headaches and nausea around 3am; emergency crews responded and found unconscious woman in another room; "exposure was caused by a furnace drawing exhaust fumes back into the building. Carbon monoxide levels in parts of the motel were eight times the acceptable level"
170 | NE | Lincoln | 2004-12-30 |  | Holiday Inn Express | Y |  | 6 |  | pool heater |  | 10 y/o girls sick at pool party in afternoon, taken to hospital; hotel evacuated; prior incident on 12/25 family of 4 sick in pool area with vomitting and headaches, complained to hotel staff and were told "their sickness likely was caused by going between the hot tub and the swimming pool"; following incident hotel installed CO detectors in the pool area
171 | LA | Baton Rouge | ?/?/2004 |  | TownePlace Suites | [6 empty] | listed on Dr. Weaver's spreadsheet, source listed as Advocate - unable to find information online
172 | OH | Sandusky | ?/?/2004 |  | Rodeway Inn | Y | [5 empty] | *listed on Dr. Weaver's spreadsheet, source listed as Blade (Toledo) - unable to find information online
173 | VA | Richmond | ?/?/2004 |  | Amerisuites | Y | [5 empty] | *listed on Dr. Weaver's spreadsheet, source listed as Richmond Times-Dispatch - unable to find information online
174 | NH | Lincoln | ?/?/2004 |  | River Green Inn | [6 empty] | *listed on Dr. Weaver's spreadsheet, source listed as Union Leader - unable to find information online
175 | TX | Waco | ?/?/2004 |  | Economy Motel | [6 empty] | *listed on Dr. Weaver's spreadsheet, source listed as Waco Tribune-Herald - unable to find information online
176 | MD | Ocean City | 2005-06-21 |  | Days Inn | Y |  | 2+ |  | hot water heater |  | incident is referenced in a subsequent CO fatality at same hotel - see case #2006-0627MD; "...several vacationers were taken to a nearby hospital and treated for exposure to carbon monoxide"; month and day of this incident is unconfirmed - one source lists "on or about June 21, 2005", another lists March 2005
177 | NM | Ruidoso Downs | 2005-07-27 | Booth family: Blayne & Lori, Alexandra, 5, and Jacob, 18 months (all injured) | AmerHost Inn & Suites |  |  | 4 | 2 injured | pool heater |  | family taken by ambulance to the hospital where they were diagnosed with CO poisoning; CO leaked "from a poorly constructed or repaired exhaust venting system related to the Motel's pool heating equipment"
178 | MT | Red Lodge | 2005-11-12 | Michael & Jennifer Butler (8 months pregnant) - both injured; Laurie White (injured - 5 months pregnant) | Rock Creek Resort |  |  | 42 |  | pool and spa heaters | basement | 200 guests attending a Marine Corps banquet, sick throughout day, 42 required transport to hospitals - 14 of them had to be flown to Billings for treatment ("at Billings Clinic, three people had to take turns in the state's only hyperbaric chamber"); victim Laurie White who was 5 months pregnant at the time of the incident gave birth prematurely a month later - the baby died two months later, premature birth was attributed to carbon monoxide poisoning; subsequent investigation by state inspectors listed "inoperable vents for the pool heaters, holes in the supply duct and other pieces of the system that did not appear to be working...new spa heater had apparently been installed in August without a mechanical permit"
179 | NJ | Clinton Town | 2005-12-16 |  | Holiday Inn | Y |  | 14 |  | generator | lower level | CO alarms went off in 2 guest rooms, 1 of which was occupied; "Members of the Clinton fire and police departments were the first to respond. At about 1am the Clinton Fire Department asked for assistance because of the high carbon monoxide readings. 'They conducted the necessary evacuation and it went great,' said Sacco (hotel manager). 'They helped provide optimal safety for the guests. It was very orderly.' Hotel operations returned to normal about three hours later, Sacco said. Also responding to the scene were the Hunterdon County Office of Emergency Management and 16 area emergency services units. The county Office of Emergency Management sent its mobile command unit and set up a command center in a parking lot near the main lobby of the hotel, said Frank Veneziala, county EMS deputy coordinator. Members of the Clinton and Quakertown fire departments checked each of the hotel's rooms with monitoring equipment...The Quakertown Fire Dept brought a large ventilator system that removed much of the carbon monoxide...by the time the Clinton squad arrived, Clinton Fire Chief Tim Langston was already checking rooms throughout the hotel...members of the Clinton Rescue Squad screened 115 people in one of the hotel's ballrooms...because of the large number of ambulances responding, a staging area was set upfor incoming ambulances at the Commerce Bank parking lot. 'We treated everyone from young to old, anyone on the floors of the affected areas,' said Chad Newsome of the Clinton Rescue Squad. 'The evacuation went well, the county got the command center set up quickly. We were very lucky. It could have been a lot worse."
180 | IA | Des Moines | 2006-02-13 |  | Sheraton Hotel | Y |  | 5 |  |  |  | injured were all employees of hotel
181 | FL | Daytona Beach | 2006-03-12 |  | Plaza Ocean Club Hotel |  |  | 7 |  |  |  | two guests taken to the hospital and diagnosed with CO poisoning; firefighters found elevated levels of CO on top two floors of the 11-story building; victims included two hotel employees; source determined to be a "leaky chimney pipe"
182 | IN | Mishawaka | 2006-04-08 |  | Country Inn & Suites | Y |  | 22 | 20 injured |  |  | Hotel manager called 911 when two children collapsed in the dining room; Fire Dept responded and found CO levels measuring 450ppm in pool room next to dining area; most of the injured were children ages 4-14 y/o; hotel was evacuated and closed until source of leak could be found
183 | NV | Yerington | 2006-04-16 | Phillip Doll, 26, Donna Vega-Robles, 30, Juan Pablo Chavez, 27, & wife Veronica Espinoza Chavez, 20 (all deceased) | Casino West Motel |  | 4 |  |  | pool heater | below victims' room | victims checked into hotel at 5:30am and were discovered about 1:15pm after hotel maintenance worker answered complaint of water leaking into room below - went upstairs and found a female victim in bathtub with water running and male victim against bathroom door; high levels of CO found in surrounding rooms; "a series of problems led to the CO expsosure"; "The heater used to warm the motel pool was not burning properly, a roof vent was not the proper height and the cap on the vent had been removed, the vents in the door to the pool equipment room had been covered with cardboard and sealed with duct tape, and the control panel had been altered such that there was no reasonable way to shut the heating unit off without disarming the power."
184 | MD | Ocean City | 2006-06-27 | Patrick Boughter, 40 (deceased) & wife Yvonne Boughter, 36 (injured) & daughters Kelly Boughter, 10 (deceased) and Morgan Boughter, 7 (injured); Betty Jo Kennell & daughters Jennifer Hagenbuch and Michelle Robertson, & granddaughter Ashley Hagenbuch, 17, and Holly Brelsford, 17 | Days Inn | Y | 2 | 7 | 1 deceased 3 injured | water heater | basement - directly below victims' room | Multiple calls to 911 from victim Yvonne Boughter who reported she and her family were ill and confused, and from additional victims in neighboring two rooms - miscommunication between responders and dispatchers resulted in medics responding to other two rooms and not the Boughter's. In addition, assumption was made that victims were suffering from food poisoning. Medics finally responded to Boughters' room 4 hours later when Yvonne came to and called 911 again, at which time both her husband and her older daughter were deceased; exhaust pipe leading from hot water heater to a vent to the outside became dislodged allowing CO to seep into 1st floor hotel rooms; boiler inspector found run of vent pipe was "way too long...which could have contributed to pipe supports collapsing and the pipe detaching"; water heater listed by manufacturer for residential use only and was not to be used in basements or under floor spaces, and it was listed as "for methane use only" but found to be running on propane; water heater was cause of a previous CO incident at this hotel on June, 21, 2005 where hotel "experienced similar problems with a hot water heater...several vacationers were taken to a nearby hospital and treated for exposure to carbon monoxide"
185 | WA | Fife | 2006-07-23 |  | Emerald Queen Hotel & Casino |  |  | 2 |  |  |  | CO detected on third floor of hotel; fire dept contacted when hotel workers smelled a "chemical" odor coming from a storage room; evaucated third and fourth floors
186 | VA | Falmouth | 2006-07-27 |  | Wingate Inn |  |  | 7 |  | boiler | first floor | 911 received hang-up call from hotel, when dispatcher called front desk back hotel clerk said guests were complaining of dizziness and lightheadedness; rescue workers evacuated hotel; CO levels at 265 ppm; highest concentrations of CO found in rooms above boiler
187 | FL | Miami Beach | 2006-10-22 |  | Hilton | Y |  | 2 |  |  |  | fire dept called when 2 guests began feeling ill; several guests tested positive for CO; building shut down for at least 3 days
188 | FL | Key West | 2006-12-21 | David Smith (injured) & wife Jody Smith (injured) & son Nathan Smith (injured) | Doubletree Grand Key Resort | Y |  | 2 |  | boiler |  | victims diagnosed with CO poisoning at hospital - see case below #2006-1227FL
189 | FL | Key West | 2006-12-27 | Thomas Lueders, 26 (deceased) & father Richard Lueders, 53 (injured); | Doubletree Grand Key Resort | Y | 1 | 7 |  | boiler | adjacent to room of decedent | Hotel manager found victims unconscious in their room after a fire alarm went off, son was on bed and father was on bathroom floor - attempted CPR and also fell ill, all three were rushed to hospital; Thomas Lueders was pronounced dead on arrival to hospital, Richard Lueders was flown to Ft Myers for treatment in hyperbaric chamber; six days before this incident, on 12/21, a family from Iowa staying on same floor called for an ambulance - presumed cause was food poisoning so no investigation - hospital diagnosed CO poisoning and later stated they "did notify the Doubletree hotel of the carbon monoxide exposure. Police rescue and fire personnel were also aware of the events."; Fire Chief said that family "rode in a boat and did other activities that could have exposed them to carbon monoxide before they fell ill"; CO leak resulted from "the leaky, fourth-floor boilers and ill-repaired ventilation system on the roof"
190 | PA | State College | 2007-08-07 |  | Residence Inn by Marriott | Y |  | 6 |  |  |  | police and emergency personnel called to hotel for report of "high levels of carbon monoxide in the pool area"; hotel evacuated and six people taken to the hospital
191 | PA | Upper Merion | 2007-09-03 |  | MainStay Suites |  |  | 4 | 3 injured | heater |  | 3 children - ages 6, 5, and 3 - and a maintenance worker became dizzy in the pool area of the hotel, children were taken to emergency room where they were diagnosed with CO poisoning; diagnosing physician called the hotel to inform them to check for "carbon monoxide issues"; Fire Dept found high levels of CO in hotel and evacuated it; "found the heater was leaking gas" as well as a "faulty chimney"
192 | CA | San Deigo | 2007-11-09 |  | Marriott Residence Inn | Y |  | 2 |  | water heater |  | housekeeper discovered victims unconscious in their beds at 2pm - they were supposed to have checked out that morning; Fire Dept responded and evacuated building; "it appears that a water heater vent pipe had come loose and filled their room with carbon monoxide"
193 | AZ | Kingman | 2007-12-17 |  | El Trovatore Motel |  |  | 4 |  |  |  | fire dept responded to a call for a "disoriented fall victim" about 8:30am and transported victim to hospital - about two hours later ER doctor contacted fire dept to inform them victim had CO poisoning and husband was still at motel; fire dept responded and evacuated a portion of motel; two other victims transported themselves to ER - article states reporter unable to determine total number of victims as hospital unable to disclose information due to confidentiality concerns; victims were extended-stay guests of motel; owner of motel "had given all tenants electric heaters, however some tried to supplement by turning on gas stoves and ovens overnight without proper ventilation"; CO levels measured at 80-110ppm
194 | PA | Allentown | 2008-01-18 | Phillip Prechtel, 63 (deceased) & wife Katherine Prechtel, 63 (injured), Jason Hannah (injured) | Best Western Allentown Inn & Suites | Y | 1 | 9 |  | water heaters | Basement - propane water heaters vented to outside, construction workers erected tent-like canopy over vent | guest called 911 was suffering "flu-type symptoms" and single ambulance responded; an hour and five minutes later 911 was called for two unconscious guests and "within 15 minutes a Level 1 Multi-Casualty Incident was declared to bring in additional ambulances"; hazmat team measured CO levels at 100ppm; CO determined to be coming from propane heaters venting to the outside properly, but their exhaust vents had been covered with a clear plastic tent to allow construction workers to repair stucco on the building's exterior; Fire Commissioner press conference: "Two police officers and three ambulance attendants who were first to arrive also were sickened...emergency personnel described a chaotic scene as they entered...while the fire alarm sounded and guests were evacuated, a woman lay on the floor of the lobby. Her skin was blue and she was barely breathing. She was being attended to by other hotel guests. The man she was staying with in Room 115 (her husband) was already dead. High levels of CO infiltrated the basement and first floor of the three-story hotel...there were no carbon monoxide detectors in the building"; the canopy erected by constructions workers "trapped gases emitted by three 80-gallon, gas-powered hot water heaters" - CO levels measured more than 400ppm in the Prechtels' room; following the incident, hotel installed CO alarms in all guest rooms; Martin Plastering was fined $2300 by OSHA for failing to detect the CO venting out of the building and for not instructing employees in identifying CO hazards.
195 | KY | Jeffersontown | 2008-01-20 |  | Comfort Suites | Y |  | 17 |  | water heater |  | guests complained of headaches, shortness of breath, nausea and vomitting; CO readings on second floor of hotel at 440+ ppm; water heater broken and serviced the day before the incident
196 | MD | Baltimore | 2008-02-02 | Luis Portillo, Sascha Schwieman (both injured) | Pier 5 Hotel Inner Harbor |  |  | 20 |  | boiler | basement | employees began feeling ill and vomiting, called 911 - Fire Dept. responded and evacuated hotel restaurant and lobby; CO levels measure at 700ppm; victims were all employees of Ruth's Chris Steak House Restaurant which was housed in the hotel; subsequent investigation found CO leaking from crack in basement boiler and that it had been emitting CO "for a period of weeks"
197 | NC | Raleigh | 2008-03-25 |  | Super 8 | Y |  | 8 |  | water heater | laundry room | five hotel guests in a vehicle flagged down an ambulance at 4:30am complaining of feeling sick; hotel was evacuated and three more guests were taken to hospital; "investigators found a heavy concentration of carbon monoxide in the laundry room"
198 | TX | San Antonio | 2008-06-22 |  | Hotel Mimosa Riverwalk |  |  | 2 | 1 injured |  |  | hotel evacuated after a guest complained of nausea and a headache and CO leak was detected; a woman and her toddler were among the injured guests
199 | VA | Virginia Beach | 2008-07-06 |  | Ocean Sands Hotel |  |  | 8 |  |  |  | Fire Dept responded after receiving calls of about guests suffering from nausea; "Crews discovered an electrical short in a spa motor had caused a ventilation fan to malfunction. The fan didn't push the carbon monoxide out of the equipment area."
200 | NY | Sweden | 2008-09-13 |  | Holiday Inn Express | Y |  | 2 |  | water heaters |  | hotel's manager pulled the fire alarm when she began to feel ill and thought she smelled gas; 73 guests evacuated; CO levels measured at 1400 ppm
201 | IA | Fort Dodge | 2009-01-31 |  | Travel Inn |  |  | 5 | 5 injured | furnace |  | five children became "lethargic and dizzy" in pool and were taken to the hospital; Fire Dept responded and found levels of CO "more than 14 times high than the safe level"
202 | NC | Huntersville | 2009-03-23 |  | Country Inn & Suites | Y |  | 2 |  |  |  | teenagers became ill - one lost consciousness - in pool area while attending a pool party
203 | WI | Green Bay | 2009-05-07 |  | Days Inn | Y |  | 2 |  | furnace |  | two guests called for ambulance thinking they had food poisoning; first responders suspected CO; firefighters pullled fire alarm to evacuate building; CO spread throughout ventilation system; officials detected levels of 800ppm on fourth floor where victims were staying, 1000ppm on the top floor - 5-story hotel; hotel windows do not open, difficult to ventilate building, leak traced to a crack in furnace
204 | MD | Ocean City | 2009-06-11 |  | El Capitan |  |  | 6 | 2 injured | pool heater | basement | Fire Dept called when a family became ill - family included mother and father, two children and two grandparents; family was staying on the first floor; investigators detected levels of CO at more than 1000ppm, evacuated building and performed a door-to-door search on each of eight floors; subsequent investigation determined the pool heater was "improperly vented"; hotel had no CO alarms and was subsequently fined $2000 by the fire marshal's office due to being out of compliance with a 2007 local law that was passed requiring them in all hotels in Ocean City, law was enacted as a result of 2006 case - see case #2006-0627MD
205 | MD | Ocean City | 2009-08-11 |  | Americana Hotel |  |  | 3 |  | see incident detail |  | police received call about guests being ill in hotel at approximately 8:20am, high levels of CO found throughout building, especially high in top three floors; police closed and evacuated hotel - firefighters conducted door to door search of 94-rom seven-story hotel; 91 of 94 rooms were occupied; some parents were seperated from their children when evacuation began; guests reported feeling ill the previous evening in their rooms; hotel owner subsequently pled guilty to failure to provide CO detectors, which were required in all hotels by a 2007 law passed following the 2006 deaths of a father and daughter (see case #2006-0627MD); owner also agreed to donate $10,000 to the Ocean City Fire Dept to help with its CO detector outreach program; cause of CO leak was never determined, fire marshal quoted one year later: "Everyone had their theory, but with several mechanical devices in bad repair at the time, we may never know the real cause."
206 | MA | Boston | 2009-09-16 |  | Liberty Hotel |  |  |  |  | boiler |  | CO alarms sounded and guests were evacuated; "Investigators tracked the problem to a boiler that had a small hole."
207 | WV | Triadelphia | 2009-12-06 | Christopher E. and Judith E. Groff, Ivan and Christine Liggett (injured) | Comfort Inn | Y |  | 4 |  | portable heaters used by construction workers |  | "construction workers employed retaining sheets and torpedo heaters to facilitate the work performed in the cold weather…caused buildup and release of carbon monoxide into guest rooms"
208 | MI | Romulus | 2009-12-28 |  | Best Western | Y |  | 2 |  |  |  | numerous guests ill - some passed out on hotel room floors, complained to staff; Fire Dept responded and evacuated hotel
209 | LA | New Orleans | 2010-01-18 |  | Ritz-Carlton |  |  | 2 |  |  |  | "buildup of carbon monoxide on some of the guestroom floors, which resulted in the evacuation of hotel guests and the treatment of some guests at nearby hospitals"
210 | FL | Daytona Beach | 2010-02-13 | Kenneth Shaw & wife Dawn Shaw (both injured) | Boardwalk Inn & Suites |  |  | 2 |  | pool heaters | parking garage below room | Victims' room was located on the first floor, directly above an enclosed parking garage; according to expert opinion in subsequent lawsuit, "brick grates originally designed to permit airflow into the garage for ventilation purposes had been blocked…allowed carbon monoxide to concentrate and enter the room through openings where plumbing lines penetrate the ceiling of the garage"
211 | TN | Chattanooga | 2010-02-14 |  | Courtyard by Marriott | Y |  | 4 |  | undetermined - possible delivery truck left running |  | hotel evacuated after 4 employees fell ill in break room in basement complaining of nausea and dizziness; one of the victims was reportedly pregnant; seven-story hotel, 120 of 128 rooms were occupied; CO may have entered hotel thru dryer vents from a delivery truck that had been left running a short distance away
212 | NH | Portsmouth | 2010-02-15 |  | Hilton Garden Inn | Y |  | 12 | 3+ injured | boiler | basement | 911 called after a worker who was found unresponsive in the basement laundry room; CO detected and hotel was evacuated; CO was measured at 600 ppm, upper floors 100 ppm; source determined to be "a malfunctioning vent in the building's heating system, located in the basement"; "unsafe levels" of CO found throughout building; injured guests included "a number of children" who were in the pool; Fire Chief "determined there to be a Level 1 mass casualty incident" calling in ambulances from five neighoring areas; Fire Dept's "portable pulse oximeter allowed firefighters to evaluate guests and workers who might have been exposed, an estimated 25-30 people, and to determine whether they needed to be brought to the hospital"; hotel installed plug-in CO detectors immediately following incident but were required to install a hard-wired system in order to comply with a new state law that mandates CO detectors in hotels
213 | NV | Reno | 2010-03-21 |  | Keno Motel |  |  | 5 |  | boiler | basement | "A metal exhaust flue that runs from the basement boiler and extends through the roof apparently was shaken loose by high winds"; CO measured at 240ppm; about 25 people live at the motel; fire dept called when several guests began feeling ill
214 | NY | Melville | 2010-06-28 | Steven Anderson (injured) | Melville Marriott | Y |  |  |  | water heater | below victim's room | two guests ill and went to hospital where they were diagnosed with CO poisoning - hospital alerted hotel who called Fire Dept; Fire Dept found elevated levels of CO in guest rooms above the boiler room; another victim reported feeling nauseous during the previous night, for period of time was unconscious on bathroom floor, awakened around 4:30pm by firefighters evacuating the building, subsequently collapsed in hallway and was taken to the hospital
215 | IA | Mt. Vernon | 2010-11-11 |  | Sleep Inn | Y |  | 3 |  | boiler |  | Firefighters called to hotel for sick guests, found "exhaust pipe for a water boiler came loose, causing carbon monoxide to escape into the building"
216 | WV | Snowshoe | 2010-12-26 |  | Seneca Lodge - Snowshoe Mountain Resort |  |  | 5 |  | water heater | basement | Fire Dept responded to call for person with chest pain and found another person with similar symptoms - determined CO was present and evacuated building; victims were all employees, 2 unresponsive when evacuated; CO levels on ground floor measured 999 ppm as high as monitors would go
217 | FL | Hialeah | 2010-12-27 | Juchen C Marctial, 19, Peterson Nazon, 17, Jonas Antenor, 18, Jean Pierre Ferdinand, 16, Evans Charles, 19 (all deceased) | Hotel Presidente |  | 5 |  | 3 deceased | car exhaust | parking garage below room | victims parked in the bottom-floor, single car garage and left car running due to low battery - the door to the interior stairway leading the room on the second floor was opened slightly, allowing the CO to seep upstairs; maid discovered the victims and called 911
218 | CA | San Francisco | 2011-01-06 |  | San Francisco Marriott Marquis | Y |  | 6 |  | water heater | restaurant next to hotel | victims were 4 guests staying in 4 separate rooms - in evening all complained of flu-like symptoms and contacted hotel doctor who recognized "there was a safety issue," hotel staff called Fire Dept who responded and found high levels of CO; two days before incident 2 seperate ambulance calls had been placed for for sick guests in same rooms but connection to CO not made; investigation led to discovery of CO leaking from a water heater in a restaurant next to hotel and drawn into hotel's air intake system
219 | ME | Portland | 2011-03-04 |  | Residence Inn | Y |  | 7 |  |  |  | Fire Dept was notified when 2 guests went to hospital experiencing nausea and headaches, evacuated hotel; high levels of CO found in rooms and hallways, some 500ppm; Fire Chief said "...exhaust fumes from the heating system were sucked into the air intake system on the building's roof. The problem seems to have been caused by a combo temperature inversion and wind currents."
220 | NY | West Seneca-Buffalo | 2011-03-12 |  | Hampton Inn | Y |  | 9 |  | heater | roof | "Police responded to a call from the front desk manager at about 5:30am yesterday after two guests asked to be moved to a new room. The couple felt dizzy and faint and had told hotel workers they believed fumes in their room were responsible." High levels of CO found on five floors of hotel; police and fire conducted room-by-room evacuation
221 | UT | St. George | 2011-04-15 |  | Comfort Suites | y |  |  |  | water heaters | third floor | hotel called gas company for "complaints of what was believed to be carbon monoxide"; gas company found high levels of CO on first, second and third floors - called Fire Dept; hotel evacuated; "some exhaust piping had separated and caused CO2 (sic) to leak onto the floors"
222 | MD | Laurel | 2011-04-30 |  | Sleep Inn | Y |  | 11 | 5 injured | pool heater |  | Fire Dept called to hotel for reports of five children complaining of headaches and nausea; discovered high levels of CO and evacuated hotel
223 | AR | Little Rock | 2011-06-09 |  | Comfort Inn | Y |  | 10 | 2 injured | pool heater |  | family of 4 (2 adults and 2 children) taken to hospital; fire dept found unsafe CO levels on all floors
224 | OR | Agate Beach | 2011-06-19 |  | Agate Beach Best Western | Y |  | 3 | 1 injured | dryer | basement laundry room | 2 employees ill in laundry room with upset stomach and dizziness, hotel called 911; Fire Dept responded with with 2 fire engines, 1 ladder truck, 1 heavy rescue vehicle and 17 firefighters; hotel evacuated and high levels of CO were detected in basement, upper floors 400-600ppm; 3 y/o girl transported to hospital
225 | OK | Norman | 2011-07-25 |  | Sooner Legends Inn & Suites |  |  | 21 |  | boiler |  | family staying at hotel took their 3 y/o to ER when he began having trouble walking and was acting intoxicated - nurse called alerted the fire dept that child may have inhaled some kind of gas; Fire Dept detected high levels of CO and evacuated building; CO found to be leaking from "a damaged ventilation pipe running from boiler to roof"; hotel owner said incident was a wake-up call and purchased CO detectors for entire building
226 | PA | Allentown | 2011-07-25 |  | Best Western Allentown Inn & Suites | Y |  |  |  | water heaters |  | 2nd incident of CO at this hotel (prior incident - see case #2008-0118PA); according to hotel, a power surge caused water heaters to malfunction leading to gas leak; CO alarms (installed after 2008 fatality) went off and all guests were evacuated safely w/o illness or injury; hotel was closed for approximately one month before receiving a certificate of occupancy allowing reopening after leak
227 | OH | Columbus | 2011-09-03 |  | Comfort Inn & Suites | Y |  |  |  | water heater | mechanical room | Guest's portable CO alarm went off in room, registering levels of 20-25ppm; manager let him into an empty room which also displayed a high reading so called fire dept who discovered a malfunctioning water heater
228 | IL | Bourbonnais | 2011-11-12 | Shawn & Jessica Hilborn & their three children; Christopher & Cortney Coombs & their 2 children | Holiday Inn Express & Suites | Y |  | 9 | 5 injured | pool heater |  | victims experienced nausea, headaches and dizziness while at pool, children lost consciousness; Fire Dept arrived and determined high levels, exceeding 300ppm, of CO in swimming pool area
229 | CT | Danbury | 2011-11-25 |  | Ethan Allen Hotel |  |  | 2 |  | boiler |  | employees smelled what they thought was a gas leak near the kitchen area and contacted authorities who told them to evacuate the building; Fire Dept arrived and found high CO levels; source of leak was an "improperly vented water boiler"
230 | WI | Green Bay | 2011-12-30 |  | Hilton Garden Inn | Y |  | 16 | 5 injured | pool heater | mechanical room | 911 called for 2 children who were sick in pool area around 9pm; when rescuers arrived, found "four small children and other victims suffering symptoms that included headache, nausea and vomitting"; more guests came forward complaining of similar symptoms; "reports show that ambulances transported a 17-year-old girl"; fire officials found CO levels at 800ppm near pool and 957ppm in adjacent equipment room, along with high levels in a workout room, a stairway and several restrooms; "The fire department also directed hotel employees to check out other guests throughout the 123-room hotel. Two staff members then took a list and proceeded to do a room-by-room search"; WI law required CO detectors at this time -- possible issue of hotel not being in compliance
231 | ND | Williston | 2012-01-29 |  | Airport International Inn |  |  | 12 | 2+ injured | boiler | pool area | guest collapsed in shower, phoned for help; ambulance arrived and called Fire Dept for assistance with hotel evacuation; many of hotel guests were parents and players of hockey team from Weyburn, Saskatchewan, Canada, who were in town for a tournament; parent whose son required oxygen treatment at hospital described the scene as "unorganized chaos...staff just continued working as if nothing had happened"; CO leak "blamed on an object being blown over a boiler vent in the hotel's pool area"; CO alarms installed following incident
232 | WV | South Charleston | 2012-01-31 | William Moran, 44 (deceased), Isaac Croy, Emmett Williams, Craig Reed, Terry Harvey, Dale & Susan Rosenbrook, Bain Edmondson (all injured) | Holiday Inn Express | Y | 1 | 16 |  | pool heater |  | Victims Moran and Edmondson were discovered deceased and unconscious/seizing, respectively, in room 511 by two co-workers who had been let into room by hotel manager when they failed to show for a morning meeting - called 911; on arrival, Fire Dept rendered aid and with police questioned co-workers about victims' previous activities, transported surviving victim to hospital and immediately began testing for CO and got reading of 317 in room; evacuated and called for additional units to do room-to-room search; found heaviest CO concentration on 3rd-5th floors ranging from 200-750ppm; Fire Dept Investigation Summary 2/12/2012: "Upon completing interviews and a thorough investigation, it has been concluded that the vent flu pipe was physically manipulated at the top to be connected to the outside vent. This was likely done when the unit was originally installed approximately 11 years ago. The removal and inspection of he old pool heater unit started the process of the vent flu pipe coming loose. The installation of the new pool heater unit further compromised the pipe. There were scratches on the piping indicating that it had been moved along the hole between floors against the concrete. Through vibration of the water filtration system and the pool heater unit, the vent flu pipe became dislodged thus creating a buildup of carbon monoxide in the open shaft area. The heat from the pool heater traveled through the vent pipe forcing the carbon monoxide to travel to rooms on both sides of the shaft and into the elevator shaft. In room 511, the heater ac unit was set to fan only so the movement of air was limited to the room. After installation of the new pool heater, there were no procedures followed as recommended by the manufacturer of that particular unit. The unit was therefore not properly tested and inspected. There were no work permits obtained prior to or during any of the work performed. The City of South Charleston Building Inspectors and the South Charleston Fire Department had no knowledge that the work procedures had occurred therefore no inspections were made."
233 | TX | Irving | 2012-03-19 | Man, pregnant woman and their three children, ages 1, 8 and 10 (all injured) | Hyatt Place | Y |  | 5 | 3 injured | boiler |  | family of five staying at hotel drove themselves to hospital due to headaches and nausea - staff at hospital diagnosed CO poisoning and contacted fire dept who responded and evacuated hotel after finding CO levels at "more than 100ppm"; multiple guests experiencing nausea, headaches and disorientation
234 | MD | Elkridge | 2012-08-27 |  | Holiday Inn Express | Y |  |  |  | heater |  | hotel evacuated after high levels of CO detected
235 | VT | Burlington | 2012-10-24 |  | Courtyard by Marriott | Y | [5 empty] | hotel evacuated "after carbon monoxide detectors signaled Burlington fire department at 7:53am"; "highest levels were on the east end of the third and fourth floors, reaching 70ppm"; hotel full with approximately 180 guests - no injuries reported; fire marshal determined "problem was apparently caused by a 'thermal inversion' - a cold, foggy air outside the hotel inhibiting the expulsion of exhaust"
236 | CA | Burlingame | 2012-11-07 | Robert McNamara, 58 (injured) | Embassy Suites Hotel | Y |  | 1 |  | boiler | pool equipment room - below victim's room | victim checked into hotel on 11/6 and when he failed to show up for a meeting on 11/7, co-workers discovered him unconscious in his room with blood and vomit coming from his nose and mouth and called 911; he was taken by ambulance to the hospital around 6:30pm - CO was suspected by ER doctor but test results were "contradictory"; medic who transported victim later returned to the hospital on an unrelated ambulance run and encountered ER physician who relayed suspicion of CO poisoning - medic reported concern to fire dept around 12:10am; fire dept went to hotel and found CO levels ranging from 20-90ppm on all nine floors - victim's room measured 990ppm; "Workers at the front desk began calling rooms. Of five called, only one responded. Concerned for the safety of the guests, authorities pulled the fire alarm and evacuated hundreds of people."; San Mateo County District Attorney's Office sued hotel alleging that "the hotel installed a boiler in a pool equipment room in 1998 without obtaining a permit from the city as a cost-saving measure. Over the next 14 years, the hotel did not properly maintain the equipment and it became clogged, holes opened in ventilation pipes and the room's configuration was changed, which prevented proper ventilation and caused a significant carbon monoxide leak." According to a news article, "A state law requiring carbon monoxide detectors in most mutliunit dwellings in California went into effect Jan 1. It was also supposed to apply to hotels and motels, but California Hotel & Lodging Association obtained a three-year extension." State law requiring alarms in hotels and motels would not go into effect until 3 years later, 2016; according to subsequent lawsuit, victim "spent three months in the hospital with severe brain damage requiring speech and physical therapy...spent three more months in an assisted living facility...relearning basic life skills, and continues struggling with irreversible brain damage"
237 | KS | Greensburg | 2012-12-09 |  | Best Western Plus Night Watchman Inn & Suites | Y |  | 34 | 3+ injured | pool heater | mechanical room | desk clerk called 911 when group of children and adults attending party at hotel reported having severe headaches and nausea; hotel evacuated, high levels of CO found in lobby and pool area related to "a water heater failing to vent properly"
238 | AR | Siloam Springs | 2013-01-21 | James Fick (injured) | Hampton Inn | Y |  | 5 |  | pool heater |  | ambulance called for 54 y/o man experiencing rapid heart rate and dizziness, 2 hours later another ambulance call for a 54 y/o man experiencing similar symptoms - emt contacted gas company, responded with police and fire who evacuated hotel; found another guest unconscious in room; "portions of the pipes connected to the heater were rusted, eroded, and deteriorating"
239 | VA | Virginia Beach | 2013-02-06 |  | Homewood Suites | Y |  |  |  | heater | roof | several 911 calls placed reporting an "unusual odor of gas"; hotel was evacuated, firefighters measured levels of carbon monoxide on several floors of the six-story hotel at 50ppm; "faulty" natural gas heater found on roof that supplied heat to common areas of hotel
240 | KS | Merriam | 2013-02-24 |  | Drury Inn | Y | [5 empty] | hotel evacuated when CO detected
241 | FL | Fort Myers | 2013-02-25 |  | Crestwood Suites |  |  | 2 |  | boiler | boiler room | 2 guests called EMS complaining of flu-like symptoms - firefighters noticed the guest room's proximity to the boiler room and checked CO levels - boiler room was 2000ppm, lobby 300ppm; cause determined to be a broken exhaust fan in boiler room; another guest staying in the room was hopitalized 4 days prior for similar symptoms "but no one made the connection to carbon monoxide exposure, and the guest was not tested."
242 | KY | Lexington | 2013-03-06 |  | Homewood Suites | Y | [5 empty] | hotel manager called 911 after a "strange odor" was noted on upper floors; Fire Dept evacuated hotel after CO levels discovered to be "over 200ppm"
243 | VA | Norfolk | 2013-03-11 |  | Tazewell Hotel & Suites |  |  |  |  | water heater | basement | Fire Dept called for possible gas leak, found high levels of CO in basement and lobby, low levels in alley behind building
244 | TN | Chattanooga | 2013-03-19 |  | Hixson Holiday Inn Express | Y |  | 2 |  |  |  | 2 housekeeping staff ill with nausea, dizziness and vomitting in basement laundry room, 911 called; Fire Dept found high levels of CO and evacuated building
245 | AL | Hoover | 2013-03-29 |  | Renaissance Ross Bridge Golf and Resort |  |  | 15 | 1 injured | pool heater | basement | family called 911 after unable to wake one of their family members - woman conscious when rescue workers arrived but rest of family, including at least one child, were all experiencing "flu-like" symptoms; firefighters found elevated CO levels in all rooms on 5th & 6th floors and ordered evacuation; reports of guests with similar symptoms earlier in the week, including a family who had checked out and returned home to Florida - Fire Dept contacted them so they could seek treatment; cause of leak found to be a "malfunction in a vent system" that vented the hotel's pool heater
246 | GA | College Park | 2013-03-31 | Laveda Green, Jamey Green, Courtney Green, Marilyn Burnett | Wyndham Garden Hotel | Y |  | 4 | 2 injured |  |  | On second morning of their stay, victims awoke in their room feeling dizzy and nauseous and one collapsed - 911 called; fire dept responded and found "elevated levels" of CO in room; victims transported to hospital; previous occupant of room reportedly had been ill as well and reported symptoms to hotel staff
247 | NC | Boone | 2013-04-16 | Daryl Jenkins, 73, (deceased) & wife Shirley Jenkins, 72 (deceased) | Best Western Blue Ridge Plaza | Y | 2 |  |  | pool heater | below victims' room | no media story until after death of another person in same room 5 weeks later (see case #2013-0608NC); victims discovered in their room by maid when they failed to show up to meet traveling companions for breakfast in lobby, man deceased in jacuzzi tub and woman unconscious on floor - declared dead on arrival to emergency room; pool heater broken/"serviced" 4 days prior to deaths (detail listed in subsequent case)
248 | NC | Boone | 2013-04-19 |  | Best Western Blue Ridge Plaza | Y |  |  |  | pool heater | two floors below victims' room/adjacent to pool | victims included 10 teenaged girls attending a pool party and staying overnight in room 325 (see case #2013-0416NC above, two victims had died of CO poisoning in room 225 but cause of death was not known at the time of this incident…cause of death not determined until death of a third victim in room 225, see case #2013-0608, at which time this incident was then publicized); after spending time in pool and lobby area, victims went to room and began feeling ill, experiencing headaches and nausea; all but one girl went home ill, and remaining occupants of room slept with the window open, notified front desk "several times" that they were all ill
249 | MN | International Falls | 2013-05-06 |  | AmericInn | Y |  | 1 |  | pool heater |  | victim found unresponsive in room (138), fire chief discovered two ambulance runs were made to the same room in a short time (April 29 and May 6); first thought illnesses were due to exposure from pool chemicals, hazmat team called and determined malfunction of pool boiler - all poolside rooms were evacuated, CO levels tested at 400-500 ppm; investigation discovered recently installed new boiler was not permitted and "size of the boiler was not proper"; other victims discovered who originally attributed symptoms to sickness and/or were moved to other rooms before symptoms advanced; following incident fire chief purchased detectors for the city's paramedics and police officers
250 | PA | Lancaster | 2013-05-10 |  | Heritage Hotel |  |  | 2 |  | boiler |  | 2 guests went to hospital experiencing "symptoms similar to carbon monoxide poisoning"; hotel was evacuated - firefighters found high levels of carbon monoxide on second and third floors
251 | NV | Reno | 2013-05-11 |  | El Cortez Hotel |  |  | 12 |  | water heaters |  | Hotel evacuated after guests began "feeling ill"; businesses on first floor of hotel also evacuated (subsequent incident at this hotel - see #2013-0601NV)
252 | WI | Oshkosh | 2013-05-13 |  | Hilton Garden Inn | Y |  |  |  |  | mechanical/ laundry equipment room | CO detector went off - first reponders found high levels of CO and evacuated hotel; 19 firefighters and five ambulances responded to assist with evacuation and checking guests for CO exposure
253 | NV | Reno | 2013-06-01 |  | El Cortez Hotel |  |  | 8 |  | "appliances" |  | Fire Dept called after guest ill; discovered elevated CO levels in basement, hotel evacuated - second incident at this hotel (see case #2013-0511NV)
254 | NC | Boone | 2013-06-08 | Jeannie Williams, 49 (injured) & son Jeffrey Williams, 11 (deceased) | Best Western Blue Ridge Plaza | Y | 1 | 1 | 1 deceased | pool heater | below victims' room | victims discovered by hotel staff when husband/father phoned front desk to ask that room be checked after victims failed to show to meet family - boy found deceased on bed, mother unconscious on bathroom floor, 911 called - fire department responded and measured CO at "lethal levels"; two deaths due to CO poisoning in same room (225) five weeks earlier (see case #2013-0416NC) - carbon monoxide suspected as cause immediately following deaths, but investigators opted to wait for results of toxicology testing on victims to confirm - not confirmed until after this incident; guests also reportedly ill on 4/19/2013 in room 325, one floor up from room 225, two floors up from pool heater; subsequent investigation revealed the following: there were no CO alarms installed in the hotel (some staff erroneously thought the combustible gas detectors and/or the smoke alarms in the rooms were CO alarms); the pool heater was housed in same room as corrosive pool chemicals; pool heater had been previously used and then moved from another hotel w/o proper permit and installed by unlicensed hotel maintenance workers and subsequently converted to natural gas against manufacturer's instructions; pool heater reportedly not working in April and had been "serviced" by a repairman who was not commercially licensed; pool heater found to be venting thru a corroded exhaust system that did not meet code standards, at the end of which was a rusted out, inoperable exhaust fan - CO leaked from exhaust system into rooms above via holes in a protective firewall
255 | NJ | Carlstadt | 2013-06-13 |  | Holiday Inn Express | Y |  | 1 |  | pool heater |  | Police and Fire responded to report of activated CO alarms at hotel and evacuated building; Carldstadt Office of Emergency Management also responded; CO levels measured at 300ppm; CO leak traced to pool heater "which recently had been repaired"; hotel staff member hospitalized; "The detectors are battery operated and not hardwired, so the staff at first thought they simply needed battery changes...after the batteries were replaced, the detectors activated again, so authorities were called"
256 | WI | Lake Delton | 2013-06-14 | Doug Schuenemann, 6 month-old son & family (all injured) | Travelodge | Y |  | 9 | 1 injured | pool heater |  | hotel employees ill and noticed CO alarm "flashing"; Fire Dept. evacuated hotel; cause of leak determined to be "blocked heat exchangers" for 2 heaters in the indoor pool area; hotel management purchased "new and additional carbon monoxide detectors" following incident
257 | CT | Glastonbury | 2013-10-29 |  | Homewood Suites | Y |  |  |  | heating unit |  | Fire Dept responded and evacuated hotel when a CO alarm went off, "traced the source to a heating unit and are ventilating it"
258 | CA | Palm Springs | 2013-11-13 | Mark Walter Ruf, 48 (deceased) | Curve Palm Springs Hotel & Resort |  | 1 | 1 |  | pool heater | below victim's room | victim discovered deceased on floor of his room by police after family had contacted them because he had not returned from his vacation; reports of guests ill in same room in weeks before victim checked in; CO exposure related to improperly vented pool heater
259 | TX | San Antonio | 2013-12-08 |  | LaQuinta Inn and Suites | Y |  |  |  |  | boiler room - fifth floor | hotel evacuated after "two guests were reportedly exposed to carbon monoxide"; Fire Dept "found carbon monoxide had accumulated from the boiler room to the fifth floor of the building"
260 | SD | Aberdeen | 2013-12-20 |  | Ramada Inn | Y |  |  |  | water heater | basement | Fire Dept called - restaurant and bar evacuated
261 | OH | Cleveland | 2013-12-28 | Amy Brill (7 months pregnant - injured) | Wyndham Hotel | Y |  | 21 | 2+ injured | boiler |  | Fire Dept and gas company responded to a call for a CO leak at 9:30am; evacuated hotel and found high levels of CO; those injured ranged in age from 9 months - 66 years, including a woman who was 7 months pregnant; the previous evening a family called front desk to report a "strange smell" in their room and hallway..."to us, it smelled like natural gas, and that's what we told the front desk...later we were told an engineer had analyzed and identified the smell as a sewer odor that was said to not be toxic or hazardous...the next morning we woke up with headaches...a short time after that, the hotel was evacuated"
262 | ID | Idaho Falls | 12/?/2013 | Jennifer Bright | Le Ritz Hotel & Suites |  |  | 1 |  |  |  | victim was employee of hotel; while at work she experienced symptoms of CO poisoning, including dizziness, nausea, fatigue and severe headaches for two months but was not told there had been a CO leak into her office until two years later; according to subsequent lawsuit "the mainline from the pool in the hotel traveled above (victim's) office...carried toxic carbon monoxide gas from the pool pump and heater...had a leak over (victim's) office"
263 | TX | Lubbock | 2014-01-16 | Harold Rutherford, 59 (deceased), Letiesha Renee Ruth, 43 (injured) | Budget Motel |  | 1 | 1 |  | wall heater | room | fire/police called by hotel when guests did not check out as expected and no answer at door; high CO levels in room and elevated CO levels in other rooms and buildings in the complex; no functioning smoke detectors; all rooms inspected had code violations involving the gas fired appliances
264 | ID | McCall | 2014-02-10 |  | America's Best Value Inn |  |  | 10 | 1 injured | pool heater |  | guests complained of headaches after being in the pool and spa area, 3-month-old infant taken by ambulance to hospital
265 | TN | Pigeon Forge | 2014-02-14 |  | Mountain Vista Inn and Suites |  |  | 2 |  | pool heater |  | victims suffered permanent injuries due to a "malfunctioning pool heating and ventilation system that emitted carbon monoxide as they slept"
266 | MD | Linthicum Heights | 2014-02-16 | Merletha McKisset, 58 (injured) | Westin | Y |  | 9 |  | water heater | laundry room - first floor | Paramedics called to hotel to help employee who felt faint, while on scene their personal CO alarm went off; hotel evacuated - elevated CO levels found throughout bldg 700-800 ppm; injured included employees and guests; cause of leak found to be damaged flue assembly for water heater
267 | ME | Ogunquit | 2014-02-23 |  | InnSeason Resorts - The Falls |  |  | 21 |  | furnace | basement | 911 called for guests experiencing headaches, nausea, dizziness and vomiting; Fire Dept discovered CO levels in building over 300ppm, evacuated hotel and called for additional ambulances; "faulty furnace" released CO into basement, carried by vents throughout the building
268 | KY | Jeffersontown | 2014-03-16 |  | Fairfield Inn & Suites | Y | [5 empty] | Carbon monoxide alarms went off and caused guests to evacuate; Fire Dept measured high CO levels throughout building, up to 400ppm; cause attributed to "malfunctioning gas burning appliance"
269 | NC | Greenville | 2014-03-18 |  | Home-Towne Suites | [6 empty] | Firefighters responded to a CO alarm activation and evacuated hotel; detected elevated levels of CO on both floors of two-story hotel
270 | MD | Cumberland | 2014-04-22 |  | Ramada Inn | Y |  |  |  | gas appliances | kitchen | Firefighters responded when "a monitor alerted" to CO in the kitchen; six-story hotel - elevated levels found on ground floor; evacuated first floor and "hotel personnel checked all (rented) rooms to make sure nobody was having a problem"; "An air-intake was blocked, so no fresh air was coming in and a belt on an exhaust fan wasn't working"
271 | PA | Crescentville | 2014-07-04 |  | Days Inn | Y |  | 5 |  | generator | basement | hotel lost power and employees turned on a generator in the basement that "filled the building with carbon monoxide"; around midnight guests ill with nausea and dizziness, hotel evacuated; five people taken by ambulance to the hospital and "dozens more made the trip on their own"
272 | PA | Dunmore | 2014-08-24 | Julie & Keith Nutt (both injured) | Best Western Plus Hotel on Tigue Street | Y |  | 30 |  | pool heater |  | guest called 911 for unconscious wife, both found unconscious in hallway by emergency responders; over 200 guests evacuated; CO found to be leaking from a cracked ventilation pipe for pool heater; multiple code violations discovered and hotel was shut down for 18 months
273 | VA | Chantilly | 2014-09-17 | Max Kipfer, 57 (injured) | Hampton Inn Dulles Airport South | Y |  | 1 |  | boiler |  | victim was sick in his room the night before, went to front desk and was given food/water then went back to room; a persistent friend kept calling his cell phone when he didn't show up for a breakfast meeting and could tell victim was incoherent - rushed to hotel and with help of manager and two maintenance workers, broke down door which was "triple locked, including with the security bar," found victim unconscious on floor; CO poisoning diagnosed at hospital
274 | WA | SeaTac | 2014-11-01 |  | Radisson Hotel | Y |  |  |  | pool heater |  | CO alarm went off and top six floors of seven-story hotel were evacuated; hotel had recently installed a carbon monoxide alarm system; firefighters found levels of CO up to "several hundred parts per million," "no reports of illness"; "the source of the CO was determined to be the swimming pool boiler system, which had recently been worked on"
275 | NC | Charlotte | 2014-11-03 |  | Sleep Inn | Y |  |  |  | "improper equipment" | 4th floor | "Firefighters, responding to an alarm, found that a sprinkler had activated on the fourth floor of the hotel due to high temperatures inside a room. In addition...the carbon monoxide detector showed a high reading"; hotel evacuated; "Investigators said a crew that was fumigating the hotel used equipment that caused carbon monoxide to form"
276 | IL | Naperville | 2014-11-10 |  | Hotel Arista |  |  |  |  | HVAC unit | roof | Fire Dept responded to report of a natural gas leak inside 12-story hotel, on arrival found "elevated natural gas and carbon monoxide readings" and evacuated hotel; leak traced to a "malfunctioning heating, ventilation and air conditioning unit on the roof of the building"
277 | AR | Rogers | 2014-11-11 |  | Candlewood Suites | Y |  |  |  | pool heater |  | hotel evacuated due to leak in pool heater
278 | ID | Preston | 2014-11-15 |  | Riverdale Resort |  |  | 19 |  | portable heater |  | victims were attendees of a family reunion, went to hospital when all began feeling ill; incident occurred in morning but emergency responders not notified of problem until 6pm, investigation was then initiated
279 | PA | Concordville | 2014-11-18 |  | Best Western Plus Concordville Hotel | Y |  |  |  | heater |  | Fire Dept responded to CO alarm - elevated CO levels in laundry area of basement as well as 1st, 2nd and 3rd floors, over 100ppm; approximately 120 guests were evacuated
280 | FL | Orlando | 2015-01-18 | Zachary Williams | Staybridge Suites |  |  | 1 |  |  |  | victim at hotel with family and began to "feel sick, weakness in his legs, rapid heartbeat, drowsiness and dizziness"; diagnosed with CO poisoning
281 | ND | Bismarck | 2015-01-18 |  | Holiday Inn Express | Y |  | 8 | 4 injured | boiler | adjacent to pool | paramedics responded to reports of children feeling ill and dizzy in pool area; victims were 4 children and 2 adults and 2 employees; hotel workers evacuated pool area prior to ambulance arrival; source of CO determined to be a boiler in room next to pool area
282 | ND | Bismarck | 2015-01-21 |  | Holiday Inn Express | Y |  | 6 |  |  |  | second incident at this hotel in 3 days - "Fire Department responded to carbon monoxide alarms going off in the building's pool and boiler rooms"; shut off gas line and reported that hotel maintenance was "working on the problem"
283 | IL | Annawan | 2015-02-15 |  | Best Western Annawan Inn | Y |  | 4 | 4 injured | pool heater |  | 4 children ill in pool area; CO levels measured at 999ppm; CO detector in pool area did not have audible alarm
284 | IA | Council Bluffs | 2015-03-22 | 15 y/o boy and 37 y/o woman (injured) | Quality Inn & Suites | Y |  | 4 | 1 injured | boiler |  | Fire Dept called to hotel for report of "several people feeling nauseated in the pool area"; firefighters found CO levels of 600ppm in pool room and guest rooms; victims were members of hotel owner's family - swimming in pool when they got sick
285 | GA | Peachtree Corners | 2015-04-13 |  | Hilton Atlanta Northeast | Y |  | 7 |  | "multiple sources" | boiler room | victims were employees who alerted fire dept they were feeling ill since early in the morning; hotel equipped with CO detectors (unclear whether they alarmed); hotel evacuated and guests relocated to other hotels after leak was determined to be coming from "multiple sources"
286 | WY | Gillette | 2015-06-03 |  | Hampton Inn | Y | [5 empty] | Gas Company notified fire dept who evacuated hotel after detecting "dangerous levels of carbon monoxide" on the third floor
287 | MA | Hyannis | 2015-07-09 |  | International Inn |  |  |  |  | boilers | basement | Fire Dept "received a call from an alarm company about an activated carbon monoxide detector sounding in the basement"; on arrival Fire Dept detected high CO levels and pulled fire alarm to evacuate building; high CO levels of "well above 100ppm" throughout building; workman had been onsite in boiler room earlier in day
288 | NY | Holtsville | 2015-08-13 |  | Ramada Plaza-Long Island | [6 empty] | Fire Dept/police called to hotel for report of "high levels" of carbon monoxide; guests and employees were evacuated to parking lot when responders arrived; "A possible source being examined is a heating-air conditioning system"
289 | IA | Sioux City | 2015-09-02 | 30 y/o woman, her two children and her parents (injured) | Corey Motel - Extended Stay |  |  | 5 | 2 injured |  |  | rescuers called to hotel on report of five people with headaches and vomiting; unit's hot water heater had reportedly stopped working earlier in the day; "source of the toxic gas was not immediately known, but an initial investigation showed it may have come from obstructed exhaust from the water heater, stove or furnace"
290 | IN | Evansville | 2015-11-13 |  | Holiday Inn Express | Y |  | 1 |  | water heater |  | employees smelled gas and called 911; hotel was fully booked for soccer tournament; Fire Dept reported natural gas leak as well as CO; "vents off water heater weren't working properly"; "The property was yellow-tagged, meaning no guest or employee was allowed inside until the repairs were made and the building commission gave the all clear."
291 | IL | Pontoon Beach | 2016-01-30 |  | Super 8 | Y |  | 4 | 4 injured |  |  | 4 children at pool party and became ill - hotel called 911; Fire Dept discovered bird's nest clogging pipe from utility room, also discovered hotel's CO detectors were not plugged in; "Officials say the problem has been fixed and all gas levels are normal. The motel has even put an external cover on the pipe in the utility room which was clogged to make sure this does not happen again. It's been recommended that it also use a hardwired carbon monoxide detector in the future."
292 | IN | Huntington | 2016-02-13 |  | Quality Inn | Y |  | 20 |  | pool heater |  | guests at party in pool room ill, some passed out; EMS arrived and evacuated building; investigation discovered "extension pipe between the indoor water heater and outdoor exhaust vent was rusted and had fallen apart" - maintenance worker had reportedly been working on the exhaust system earlier that day
293 | OH | Austintown | 2016-03-11 |  | Sleep Inn | Y |  | 18 | 2+ injured | pool heater |  | EMS called to hotel for child who had fallen in pool area - responders carry CO alarms on their EMS bags, which began alarming; CO levels at 600ppm; high levels in pool area and upper levels of hotel; Fire Chief reported "the biggest struggle was was getting everyone out...we set the fire alarms off and people just ignored them"
294 | MO | Sunset Hills | 2016-04-08 |  | Hampton Inn | Y | [5 empty] | gas company, fire and police responded to report of gas leak at hotel in pool area, evacuated hotel
295 | NY | Queensbury | 2016-04-20 |  | Six Flags Great Escape Lodge |  |  |  |  | boiler | basement | hotel evacuated when CO alarm went off; Fire Dept found "slightly elevated" levels of CO in the basement; "an issue with a boiler intake was found and repaired"
296 | NY | Queensbury | 2016-04-21 |  | Six Flags Great Escape Lodge | [6 empty] | 2nd incident of CO at this hotel, 1st on 4/21/2016 - hotel evacuated when CO alarm went off
297 | ME | Portland | 2016-06-06 |  | Howard Johnson | Y |  | 1 |  | furnace | below victim's room | EMS called for ill guest; rescue crews found a man "unconscious and vomiting in a stairwell"; CO alarms on EMS bags alerted to high levels of CO; CO levels of 400ppm - highest level was found in room of ill guest, located above the "furnace room"; hotel reportedly equipped with CO detectors but unclear whether they alarmed
298 | MI | Warren | 2016-07-25 |  | Hawthorn Suites by Wyndham | Y |  | 2 |  | boiler |  | A couple and their dog were found unconscious in their room by hotel housekeeper; CO levels of 439 ppm were detected; cause of CO reportedly associated with boiler and "melted pipes and wires"; quote from fire commissioner: victims "reportedly check out at 11:30am and were found when an employee later went to clean the room...the husband went down and checked out...went back up to the room to get his wife. For whatever reason, we don't know if he became disoriented, he decided to lay down also. If he hadn't checked out, and the maid hadn't gone to his room, we would have been looking at a tragedy."
299 | NC | Morganton | 2016-08-17 |  | Comfort Inn | Y | [5 empty] | "a hot water heater caused a sprinkler to go off in a room that houses the hotel's electrical equipment" - first responders detected "high levels" of CO on every floor and evacuated building
300 | MA | Andover | 2016-08-26 |  | LaQuinta Inn and Suites | Y | [5 empty] | CO alarm sounded, Fire Dept responded and evacuated hotel; CO levels measured at over 100ppm in laundry room; "Columbia Gas has determined what appliancese caused the high levels of CO to be emitted and have subsequently shut them down. The gas inspector is on scene to determine how to best replace the problematic units."
301 | NJ | Bridgewater | 2016-09-08 |  | Days Inn | Y |  | 1 |  | water heaters |  | hotel evacuated after CO alarm sounded; "hotel employees went door-to-door to make sure all of the rooms were cleared"; 1 firefighter hospitalized due to CO; "firefighters discovered that water heaters were to blame for the elevated CO. PSEG was called in to cap the heaters"; hotel was issued a violation
302 | MA | Springfield | 2016-10-18 |  | Marriott Hotel | Y |  |  |  | boiler |  | two floors evacuated after "unsafe" levels of CO related to a malfunctioning boiler; approximately 50 guests evacuated from sixth and seventh floors; CO levels measure at 3000 ppm on both floors
303 | DE | Dover | 2016-11-05 |  | Home2 Suites by Hilton | Y | [5 empty] | Fire Dept responded to a CO alarm, found elevated CO levels on 4th floor - pulled fire alarm to evacuate hotel; on further investigation found "dangerously high levels in the pool heater room"; another leak found in utility area at opposite end of building
304 | CO | Durango | 2016-12-20 |  | Residence Inn | Y |  | 2 | 2 injured | pool boiler |  | Fire Dept responded and evacuated hotel; 2 boys who had been playing in pool area were hospitalized for CO poisoning; some hotel staff experiencing headaches; source of CO determined to be pool boiler, "the owners intend to replace the entire boiler unit"; "They did have carbon monoxide detectors throughout the hotel, but unfortunately, the one in the pool area was defective"
305 | NC | Asheville | 2016-12-23 |  | Clarion Inn | Y |  |  |  | pressure washers | outside hotel | Fire Dept called to hotel at 2:15am for high levels of CO, evacuated building; CO caused by hotel staff using gas powered pressure washers outside building - the "HVAC system sucked the carbon monoxide into the building"
306 | WI | Lake Delton | 2016-12-28 |  | Sunset Bay Resort |  |  |  |  | water heater | basement | CO alarm went off and guests evacuated without incident; "Fire officials said the incident is a good reminder to businesses and homeowners to install and regularly test CO detectors in any place where there are gas fired appliances."
307 | NY | Plattsburgh | 2017-01-07 |  | Comfort Inn & Suites | Y |  |  |  | heating unit | neighboring restaurant kitchen | hotel CO alarm sounded about 4:00am and firefighters responded to hotel; found CO source to be malfunction of a heating unit in restaurant next door; the hotel's five rooms in the area of the restaurant were evacuated to lobby of hotel while firefighters investigated
308 | TX | Corpus Christi | 2017-01-10 |  | Omni Hotel |  |  | 6 |  | pool heater |  | victims were hotel staff who complained of lightheadedness and nausea, Fire Dept called and victims were transported to hospital; hotel was evacuated; high levels of CO found on lower floors; "Smaller levels of gas were detected on some of the hotel's higher floors, following the path of the elevator shafts"
309 | MD | Clear Spring | 2017-03-02 |  | Sleep Inn & Suites | Y |  |  |  | pool heater |  | Ambulance crew called to assist a guest with a medical condition, their personal CO detectors alarmed alerting them to a CO leak that was subsequently traced to a propane pool heater
310 | MA | Mansfield | 2017-03-27 |  | Holiday Inn | Y |  |  |  | pool heater |  | hotel evacuated and fire dept called when CO alarms went off around 6pm; CO levels measured at 800ppm on first floor; high CO levels detected in a mechanical room and on the first and second floors near and above the pool heater; "heaters for the pool and whirlpool were shut down and the cause is being investigated"
311 | MI | Niles | 2017-04-01 | Bryan Watts, 13 (deceased) | Quality Inn & Suites | Y | 1 | 13 | 1 deceased 6 injured | pool heater |  | a hotel employee discovered 6 children unconscious in pool area, EMS called and hotel was evacuated; 1 child found unconscious in a first floor room; CO levels measured at 800ppm; additional victims were hotel staff and first responders; cause determined to be "a pool heater ventilation pipe disconnecting from the pool heater. This likely caused carbon monoxide to leak into an enclosed pool maintenance room. An exhaust system in the pool maintenance room vented out of the room and into the enclosed pool area."
312 | MD | Baltimore | 2017-04-08 |  | Marriott Delta Hotel | Y |  | 2 |  |  | basement | Fire Dept called after CO leak detected in basement; hotel evacuated; two guests transported to hospital
313 | MI | Novi | 2017-04-26 |  | Novi Oaks Hotel |  |  |  |  | pool heater |  | hotel worker ill and called 911; hotel was evacuated after Fire Dept detected high levels of CO; mechanical inspector determined "a pool heater had improper ventilation"
314 | AR | Bentonville | 2017-05-01 |  | Holiday Inn Express | Y |  |  |  | "construction related issues" |  | Fire Dept called after CO alarms went off at hotel around 8am; hotel evacuated; source of CO was listed as "construction related" - hotel is "being renovated and a construction crew was putting a roof on the building"
315 | ND | Fargo | 2017-05-29 |  | LaQuinta Inn and Suites | Y |  | 11 | 2+ injured |  |  | 9 y/o girl transported to hospital after getting sick in pool area, 10 other guests sought medical attention; Fire Dept responded and detected CO levels at 300ppm in pool area and hallways; cause not immediately apparent but pool heater suspected
316 | VA | Warrenton | 2017-07-24 |  | Holiday Inn | Y | [5 empty] | hotel evacuated due to "very high levels" of CO; Fire Dept "said the source of the carbon monoxide has been narrowed down to gasoline powered equipment"
317 | CA | Chico | 2017-07-27 |  | Marriott Residence Inn | Y |  | 2 |  | water heater | next to victims' room | ambulance called for two guests experiencing headaches, dizziness and nausea - transported to hospital; hospital diagnosed CO poisoning and alerted fire dispatch; Fire Dept responded to hotel and evacuated remaining guests; CO levels in victims' room measured at 150ppm, in adjacent room that housed water heater levels measured 550ppm
318 | TX | Perryton | 2017-08-24 | Patricia, 58, (deceased) & husband David Ivie, 62 (deceased) | Best Western | Y | 2 | 5 |  | pool heater | below victims' room | victims discovered unconscious in their room (217) by housekeeper when she heard CO alarm sounding in room - woman was on bed, man was on floor; hotel evacuated; Fire Dept found "substantial levels" of CO in parts of the hotel; firefighters discovered that guests in room located four doors down from room 221 had taken the battery-powered CO alarm off the wall and placed it on the nightstand with a note stating the alarm went off at 3:30am and 4:30am and said the battery needed replacing; Patricia Ivie died from her injuries two months later, and David Ivie died of his injuries four months later
319 | NC | Fayetteville | 2017-11-07 | Michael Brown (injured) & wife | Marriott Residence Inn | Y |  | 3 |  | water heater | first floor | Two guests woke up not feeling well and went to the hospital, found to have elevated levels of CO; hospital notified fire dept who evacuated hotel; victim Michael Brown said he began having symptoms the day before at hotel and collapsed, taken to hospital but released later and returned to his hotel room - CO poisoning not diagnosed until he collapsed again the following day, wife found him unconscious and took him back to hospital; they both were transferred to a nearby hospital for treatment in hyperbaric chamber; "Investigators said the hotel has carbon monoxide detectors, but they did not go off. Instead someone had to pull the fire alarm to evacuate guests." Cause of CO leak was determined to be a "malfunctioning water heater in a mechanical room on the first floor."
320 | WI | Madison | 2017-11-11 |  | Doubletree Hotel | Y |  | 8 |  | pool boiler |  | Fire Dept responded to call for two guests who passed out in the stairwell by the pool; when they arrived, a CO sensor in their EMS bag began sounding; evacuated area and found CO levels at 150ppm in stairwell, 400ppm in pool room, and 2000-2500ppm inside boiler room for the pool; gas company determined "an exhaust pipe on one of the boilers had fallen off and was discharging exhaust into the room."
321 | TX | Temple | 2017-12-14 |  | Hilton Garden Inn | Y |  | 2 |  |  |  | EMS called for two guests complaining carbon monoxide related symptoms, transported to hospital; firefighters "located and confirmed the source of the carbon monoxide"
322 | MD | Baltimore | 2018-02-01 |  | Delta Hotel |  |  |  |  | underground electrical fire | near hotel | underground electrical fire in a manhole near the hotel; Fire Dept reported "high levels" of CO in the sub-basement of the hotel; "firefighters monitored all levels of the hotel with guests to ensure the levels of carbon monoxide were safe"
323 | NY | NYC-Manhattan | 2018-02-21 |  | The Hotel on Rivington |  |  |  |  | underground fire |  | hotel and three neighboring buildings evacuated due to CO created by "manhole fires"; CO levels measured at 1400ppm
324 | TX | Austin | 2018-02-21 |  | Fairmont Hotel |  |  | 2 |  | oven | kitchen | hotel new and set to open in next few weeks; Fire Dept called to hotel for reports of a gas leak; found "high levels" of CO on first seven floors and evacuated workers; CO related to pizza oven in hotel's kitchen, "An exhaust system had failed, forcing the harmful gas to recirculate into the hotel's air conditioning system"; 2 hotel workers hospitalized
325 | MO | Watford City | 2018-03-10 |  | Little Missouri Inn & Suites |  |  | 3 | 3 injured | pool heater |  | 911 called for children in pool area having difficulty breathing; Fire Dept responded and determined CO exposure resulting from "a malfunction in the pool mechanic room ventilation system"
326 | CO | Denver | 2018-05-22 |  | Aloft Hotel (Marriott) | Y |  | 18 |  |  |  | Rescuers called to hotel when a CO alarm went off (news article does not reference if it was hotel alarm but a reader comment states "The hotel did not detect the carbon monoxide, hotel guests did with their own equipment"); hotel evacuated, victims transported to hospital by ambulances and a hotel van
327 | NH | Windham | 2018-06-04 |  | Manor Motel - extended stay |  |  |  |  | furnace | mouse nest in exhaust pipe | motel manager quoted, "We had a carbon monoxide detector in the basement, in the laundry area…and the alarm was going off and one of the guests was nice enough to call me and tell me that she could hear..an alarm going off"; motel fully occupied and approximately half were evacuated due to leak; fire dept detected 2000ppm near the exterior of ventilation system and elevated levels inside some rooms; mouse nest discovered in exhaust pipe; "technician cleaned out the system and was working on replacing the piping going out of the building"
328 | VA | Hampton | 2018-06-06 |  | Quality Inn | Y |  |  |  | water heater |  | firefighters responded and evacuated building
329 | TX | San Antonio | 2018-07-24 |  | Comfort Suites | Y |  | 12 |  | water heater |  | 911 call at 1:40am for "a group" reporting they were ill from food poisoning; additional call for a second family with same symptoms prompted firefighters to check air quality; "found an exhaust pipe on a water heater that was disconnected and the exhaust was being sucked up by the room handlers"; "Investigators at the scene told reporter that the hotel did not have carbon monoxide detectors as local rules do not require it in hotels or motels"
330 | IA | Ankeny | 2018-07-28 |  | Fairfield Inn & Suites by Marriott | Y |  | 3 |  |  |  | One of three victims staying in same room was ill with dizziness and nausea, called for ambulance at approx 2am; emergency responders arrived and found all three victims ill, detected CO levels at 500ppm; additional ambulances called, hotel evacuated; gas company response; source of CO "faulty venting from the laundry"
331 | CO | Longmont | 2018-10-29 |  | Super 8 | Y |  | 1 |  | water heater | boiler room | Fire Dept responded to 2am call for guest who was feeling ill, transported to hospital where guest was "eventually" diagnosed with CO poisoning - hospital notified fire dept who then returned to the hotel and evacuated guests; high levels of CO found throughout building
332 | NC | Jacksonville | 2018-11-02 |  | Holiday Inn Express | Y |  | 16 | 1 injured |  |  | police called to hotel around 3am for a strange odor, discovered high levels of CO and evacuated building; guests included victims of Hurrican Florence who had been displaced from their homes as well as federal employees in town to help hurricane victims
333 | TN | Nashville | 2018-11-07 |  | Westin | Y |  | 14 |  | heater |  | front desk called 911 when multiple guests from gym on third floor complained of feeling ill; firefighters responded and evacuated third and fourth floors of hotel; "A state ordinance, adopted by the city, only requires carbon monoxide detectors on floors where guests sleep. The third floor only housed a pool and the workout room."
334 | CO | Boulder | 2018-11-18 |  | Hyatt Place Boulder | Y |  | 1 |  | boiler |  | leak discovered when guest was hospitalized with CO poisoning - hospital contacted Fire Dept. who then evacuated hotel; CO levels measured 50ppm in lobby, 2nd-5th floor rooms had levels "up to 200ppm", 500ppm in boiler room; "maintenance engineer of the hotel initially told firefighters the hotel did not have any gas feeds to the hotel, but firefighters said there was a gas-fed boiler room that was the source of the carbon monoxide"; "fire department also directed the hotel to contact guests who had been staying at the hotel in the three days leading up to the evacuation to determine if any of them had symptoms"
335 | MA | Foxborough | 2018-12-17 |  | Renaissance Patriot Place Hotel | Y |  | 1 |  | boiler |  | CO detectors alerted staff to elevated CO levels; 60-70 guests and employees were evacuated from building by fire dept; "airing-out process took a while because the windows at the hotel do not open"
336 | NY | Syracuse | 2019-01-01 |  | Genesee Grande Hotel |  |  | 5 |  | boiler |  | CO alarm on first floor went off, manager "then went to the carbon monoxide reader in the basement and called 911"; Fire Dept. responded and evacuated "19 occupied rooms"; source of CO leak listed as "a faulty heating boiler"
337 | MI | Charlevoix | 2019-01-01 |  | AmericInn | Y |  | 12 |  | pool boiler |  | Fire Dept called to hotel for high carbon monoxide levels in the pool area; pool had no CO detector but when guests complained of feeling ill, staff brought one from another area - it alarmed and they called 911; CO levels measured at 90ppm in pool area; users of pool were guests and community members, hotel had opened pool up for community use to celebrate New Year's Day
338 | CO | Aurora | 2019-01-29 |  | Gaylord Rockies Resort & Convention Center |  |  | 2 |  |  | boiler room | Fire Dept responded to report of high levels of CO at convention center; according to hotel spokesperson, "high carbon monoxide levels were determined to be related to work taking place on the property…in the boiler room"
339 | CO | Aurora | 2019-01-30 |  | Gaylord Rockies Resort & Convention Center | [5 empty] | boiler room | Fire Dept responded to reports of high levels of CO in same area as previous day (see previous case); no injuries reported
340 | NJ | Carneys Point | 2019-02-15 |  | Friendship Motel Inn |  |  | 7 |  |  |  | Authorities responded to hotel for a deceased child "who was 7 or 8"; police suspected CO poisoning and evacuated building; a family of 6 had elevated levels of CO in their blood and were taken to the hospital, a 7th guest had elevated levels but declined treatment; medical examiner ruled out CO poisoning as cause of death of child because "the child had been being treated for an infection prior to her death"; "The only source of gas in the motel was its gas hot water heater in the basement...but readings in the basement showed no excess carbon monoxide...it's possible a resident was cooking in a room"
341 | SD | Pierre | 2019-03-15 |  | Baymont Inn & Suites |  |  |  |  | furnace |  | Fire Dept responded at 3:24am after CO alarm alerted hotel staff; evacuated building; CO levels measured 40-60ppm, "extremely high" levels in fitness room; cause determined to be "a gas burning furnace whose exhaust outlet had been blocked by snow…a drift had covered up the vent"
342 | MA | Saugus | 2019-04-07 |  | Holiday Inn Express | Y | [5 empty] | Fire Dept responded, hotel evacuated
343 | VA | Norfolk | 2019-04-07 |  | Quality Inn Suites | Y |  | 1 |  | pool heater |  | Fire Dept called at 7:25pm for report of a CO leak, first floor evacuated
344 | NE | Omaha | 2019-05-10 |  | Comfort Inn Suites | Y | [5 empty] | Fire Dept responded, hotel evacuated
345 | WY | Gillette | 2019-05-12 |  | Travelodge by Wyndham | Y |  |  |  | water heater |  | Fire Dept responded "for a carbon monoxide detector activation…determined there was a malfunction with the water heater for the laundry facility"
346 | PA | Erie | 2019-05-25 |  | Days Inn | Y |  | 2 |  |  |  | Fire Dept evacuated hotel around 5pm; one victim found unresponsive
347 | MT | Butte | 2019-07-13 |  | Quality Inn Hotel & Suites | Y |  | 23 |  | pool boiler |  | Ambulances responded to hotel at 7:30am after reports of three people ill with symptoms including "throwing up, red skin, dizziness and headaches"; "(victim) says guests weren't alerted with carbon monoxide alarms"
348 | NY | Brooklyn | 2019-07-17 |  | Insignia Hotel |  |  |  |  | transformer fire | manhole near hotel | hotel guests evacuated by Fire Dept at approx 10pm due to "a smoking manhole outside which caused high carbon monoxide levels inside the hotel" (spokesperson for power company); according to one guest, "We heard fire alarms, we saw the fireman outside. They weren't really doing anything until a few hours later when the carbon monoxide started coming in, and then they started to evacuate us"
349 | FL | Estero | 2019-07-27 |  | Hilton Garden Inn | Y |  |  |  | boiler |  | Fire Dept responded to a "gas alarm" and evacuated hotel
350 | SC | Myrtle Beach | 2019-08-26 |  | Hampton Inn | Y | [5 empty] | Fire Dept called to hotel for "reports of a carbon monoxide leak"; elevated levels of CO found on all floors, hotel evacuated; highest reading at 100ppm; according to Fire Chief, "work was being done on the laundry machines and that may have been the cause of the carbon monoxide leak...maintenance crews would have to find and fix the leak"
351 | SC | Myrtle Beach | 2019-09-10 |  | Hampton Inn | Y | [5 empty] | (second response to this hotel - see above) Fire Dept responded to hotel at 9:50am and found elevated CO levels at 100ppm; "(gas company) is taking a closer look at what the root of the issue is…say the hotel did make repairs after the last leak, and it's still unclear if the two events are related"
352 | OH | Columbus | 2019-09-17 |  | Home2 Suites by Hilton | Y |  | 2 |  | gas saw |  | 2 victims hospitalized; CO exposure due to "a worker using a gas saw in a confined area"
|  | Total # of incidents | 352 |  |  | Total # deaths (includes children) | 159 |  | Total# injured (includes children) | 2294
[8 empty] | Total # child deaths | 26 | Total # children injured | 207
Please help protect others by sharing this information
Be informed
To date, there is no federal requirement for the installation of carbon monoxide alarms in hotels. Only 14 states require installation of CO alarms in hotels and motels under statute (www.ncsl.org). There currently are no federal requirements for carbon monoxide education and/or training of hotel owners and staff. No federal agency tracks CO incidents in U.S. hotels.
Be aware and be safe when traveling
Know the symptoms of carbon monoxide poisoning (you can't see it, smell it or taste it) and always carry your own carbon monoxide alarm when you travel. Alarms are sold online and in stores anywhere you find household smoke alarms.
About this spreadsheet
This is not an all inclusive list of hotel/motel CO incidents, these are only the cases that had an associated media story, or were otherwise noted in a publicly accessible document online. Cases, both old and new, are added as they are discovered.
All incidents and details listed were obtained via media accounts and publicly accessible documents. Those marked with * are courtesy of Dr. Lindell Weaver, author of the 2007 published article "Carbon Monoxide Poisoning at Motels, Hotels and Resorts" (Amer. Journal of Preventive Medicine)
"Carbon Monoxide Poisonings in Hotels and Motels: The Problem Silently Continues" published in 2019 (Preventive Medicine Reports) by authors Dr. Neil Hampson, Dr. Lindell Weaver, Kris Hauschildt, and Kayla Deru, along with the 2007 article referenced above, provides collective published data on U.S. hotel CO incidents, 1989-2018.
To add a case or additional information to this log, or to request an updated copy please email krishauschildt@yahoo.com
This spreadsheet was compiled and is maintained by Kris Hauschildt in memory of Daryl & Shirley Jenkins and Jeffrey Williams who lost their lives to carbon monoxide poisoning in the same hotel room just a few weeks apart on April 16 and June 8, 2013.
CO exposure limits
(over an 8-hour time-weighted average)
OSHA: 50ppm
Occupational Safety and Health Administration
NIOSH: 35ppm
National Institute for Occupational Safety and Health
ACGIH: 25ppm
American Conference of Govt Industrial Hygienists
WHO: 8ppm
World Health Organization